## I (hidden)
[25 empty] | HONEYWELL | MOTOR SHAFT POWER & CURRENT | [5 empty] | DIMENSIONS | WEIGHT
[9 empty] | 5 | [15 empty] | OS. NO. | Constant torque |  |  | Variable torque |  |  | W x H x D
[26 empty] | P [HP] |  |  | P [HP] |  | Enclosure
[25 empty] | Date: 05/20/1999 | Pct | Ict | IMAX | PVT | ISQR | M/NEMA 1 | W*H*D | lbs
| Inverter Selector | [5 empty] | adjust | 0
|  |  |  | CXL INDEX |  | 1 | [15 empty] | 0
| 1 | 1.6662 | $ | 1 | CXL | 6 |  | 0200 | 1 | 3 | 1 | 5 | 1 | G | 1 | 5 |  | 1 | I | 1 | 0 | 1 | Machine | 1 | Select model
[25 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | Y/N
[5 empty] | TYPE |  |  | KW |  | PHASE |  | VOLTAGE |  | PANEL |  | IP |  |  | FILTER |  | BRAKE |  |  |  | OS NUMBER | MODUTROL IV TRADE REPLACEMENT | TRANSFORMER | AUX SWITCH REQS | ACCESS-ORIES | STROKE SETTING | AUX SWITCH SETTINGS | VOLT (Vac) | TORQUE (lb-in, lb-ft) | STROKE MAX (DEGREES) | TIMING MAX (SECS) | AUX SWITCHES | MOTOR SHAFTS | ADAPTOR BRACKET | CONTROL SIGNAL | FUNCTIONAL REPLACEMENT | TRADE COMMENTS | MOD IV
|  |  |  | 1 | CXL | 3 | 1 | 0030 | 1 | 3 | 1 | 500 | 1 | G | 1 | nema 12 | 5 | 1 | I | 1 | 0 | 1 | Machine | 1 | Select model | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
|  |  |  | 1 | CXL | 3 | 1 | 0030 | 1 | 3 | 1 | 500 | 1 | G | 1 | nema 12 | 5 | 1 | I | 1 | 0 | 1 | Machine | 2 | 3402--7 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 25 | 110° | N/A | N/A | N/A | N/A | N/A | M8415A1004 | N/A | FALSE
|  |  |  | 2 | CXS | 5 | 2 | 0050 |  |  | 2 |  |  |  | 2 | nema 1 | 7 | 2 | C | 2 | 1 | 2 | Fan/Pump | 3 | 3402A--7 | N/A | N/A | N/A | N/A | N/A | N/A | 120 | 25 | 110° | N/A | N/A | N/A | N/A | N/A | NDR | N/A | FALSE
| Country | Exchange |  |  |  | 7.5 | 3 | 0075 | [9 empty] | 3 | [5 empty] | 4 | 3403--4 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 25 | 110° | N/A | N/A | N/A | N/A | N/A | M8405A1006 | N/A | FALSE
1 | USA | 1.6662 | $ |  |  | 10 | 4 | 0100 | [15 empty] | 5 | 3405--11 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 25 | 90° | N/A | 1 | N/A | N/A | N/A | M836A1042 | N/A | FALSE
2 | Germany | 3.0155 | DM |  |  | 15 | 5 | 0150 | [15 empty] | 6 | 3405--14 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 25 | 90° | N/A | 1 | N/A | N/A | N/A | M836A1042 | N/A | FALSE
3 | France | 10.1025 | Fr |  |  | 20 | 6 | 0200 | [15 empty] | 7 | 3405--2 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 20 | 90° | N/A | N/A | N/A | N/A | N/A | M836A1042 | N/A | FALSE
4 | Netherlands | 3.3989 |  |  |  | 25 | 7 | 0250 | [15 empty] | 8 | 3405--3 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 25 | 90° | N/A | N/A | N/A | N/A | N/A | M836A1042 | N/A | FALSE
5 | Japan | 230.4564 |  |  |  | 30 | 8 | 0300 | [15 empty] | 9 | 3405A--11 | N/A | N/A | N/A | N/A | N/A | N/A | 120 | 25 | 90° | N/A | 1 | N/A | N/A | N/A | M436A1116 | N/A | FALSE
6 | Canada | 2.4435 |  |  |  | 40 | 9 | 0400 | [15 empty] | 10 | 3405A--2 | N/A | N/A | N/A | N/A | N/A | N/A | 120 | 25 | 90° | N/A | N/A | N/A | N/A | N/A | M436A1116 | N/A | FALSE
7 | E.C.U. | 1.5212 |  |  |  | 50 | 10 | 0500 | [15 empty] | 11 | 3420--4 | M9185D1004 | N/A | N/A | N/A | N/A | N/A | 24 | 25 | 90° | N/A | N/A | N/A | N/A | N/A | M9185D1004 | N/A | FALSE
8 | HEDC | 1.5212 |  |  |  | 75 | 11 | 0750 | [15 empty] | 12 | 3420A--4 | M9185D1004 | 50017460-003 | N/A | N/A | N/A | N/A | 120 | 25 | 90° | N/A | N/A | N/A | N/A | N/A | M9185D1004 | N/A | FALSE
9 | Belgium | 62.1832 |  |  |  | 100 | 12 | 1000 | [15 empty] | 13 | 3430-18 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 25 | 90° | 25 | N/A | N/A | N/A | N/A | NDR | N/A | FALSE
10 | Italy | 2975.3571 |  |  |  | 125 | 13 | 1250 | [15 empty] | 14 | 3430-21 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 25 | 90° | 25 | N/A | N/A | N/A | N/A | NDR | N/A | FALSE
11 | Switzerland | 2.5366 |  |  |  | 150 | 14 | 1500 | [15 empty] | 15 | 3430--7 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 25 | 90° | N/A | N/A | N/A | N/A | N/A | M7415A1006 | N/A | FALSE
12 | Sweden | 13.3019 | [21 empty] | 16 | 3440--4 | M9184D1021 | N/A | N/A | N/A | N/A | N/A | 24 | 100 | 160° | 30 | N/A | N/A | N/A | N/A | M9184A1019 | N/A | FALSE
13 | Denmark | 11.4807 | [21 empty] | 17 | M110AAB-1 | M8185D1006 | 50017460-003 | 220736A | N/A | ADJ | N/A | 120 | 25 | 45-270° | 60 | 1 | N/A | N/A | N/A | NDR | N/A | FALSE
14 | Australia | 2.6783 | [21 empty] | 18 | M110AGA-1 | M8185D1006 | N/A | N/A | N/A | ADJ | N/A | 24 | 25 | 45-270° | 60 | N/A | N/A | N/A | N/A | NDR | N/A | FALSE
15 | Finland | 9.167 | [21 empty] | 19 | M110AGB-1 | M8185D1006 | N/A | 220736A | N/A | ADJ | N/A | 24 | 25 | 45-270° | 60 | 1 | N/A | N/A | N/A | NDR | N/A | FALSE
16 | Norway | 12.7992 | [21 empty] | 20 | M110GGA-1 | M9185D1004 | N/A | N/A | Q7230A1005 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | NDR | N/A | FALSE
17 | Autria | 21.2012 | [21 empty] | 21 | M110JGA-1 | M9185D1004 | N/A | N/A | N/A | ADJ | N/A | 24 | 25 | 65-270° | 60 | N/A | N/A | N/A | N/A | M9185D1004 | N/A | FALSE
18 | UK | 1 | £ | [20 empty] | 22 | M110JGB-1 | M9185D1004 | N/A | 220736A | N/A | ADJ | N/A | 24 | 25 | 65-270° | 60 | N/A | N/A | N/A | N/A | M9185D1004 | N/A | FALSE
[24 empty] | 23 | M110QGA-1 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | NDR | N/A | FALSE
[24 empty] | 24 | M120AAA-1 | M6184D1035 | 50017460-003 | N/A | N/A | ADJ | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | NDR | N/A | FALSE
[24 empty] | 25 | M120AAB-1 | M8185D1006 | 50017460-003 | 220736A | N/A | ADJ | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | NDR | N/A | FALSE
[24 empty] | 26 | M120AAC-1 | M6184D1035 | 50017460-003 | 220736B | N/A | ADJ | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | NDR | N/A | FALSE
[24 empty] | 27 | M120AGA-1 | M6184D1035 | N/A | N/A | N/A | ADJ | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | NDR | N/A | FALSE
[24 empty] | 28 | M120GGA-1 | M9164D1009 | N/A | N/A | Q7230A1005 | ADJ | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | NDR | Select signal range | FALSE
[24 empty] | 29 | M120JAA-1 | M9164D1009 | 50017460-003 | N/A | N/A | ADJ | N/A | 120 | 35 | 65-270° | 60 | N/A | N/A | N/A | N/A | M9164D1009 | N/A | FALSE
[24 empty] | 30 | M120JAC-1 | M9164D1009 | N/A | 220736B | N/A | ADJ | N/A | 24 | 35 | 65-270° | 60 | 2 | N/A | N/A | N/A | M9164C1068 | N/A | FALSE
[24 empty] | 31 | M120JGA-1 | M9164D1009 | N/A | N/A | N/A | ADJ | N/A | 24 | 35 | 65-270° | 60 | N/A | N/A | N/A | N/A | M9164A1005 | N/A | FALSE
[24 empty] | 32 | M120QGA-1 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | NDR | N/A | FALSE
[24 empty] | 33 | M130AGA-1 | M8185D1006 | N/A | N/A | N/A | ADJ | N/A | 24 | 50 | 45-270° | 60 | N/A | N/A | N/A | N/A | NDR | N/A | FALSE
[24 empty] | 34 | M130AGB-1 | M8185D1006 | N/A | 220736A | N/A | ADJ | N/A | 24 | 50 | 45-270° | 60 | 1 | N/A | N/A | N/A | NDR | N/A | FALSE
[24 empty] | 35 | M130GGA-1 | M9185D1004 | N/A | N/A | N/A | ADJ | N/A | 24 | 50 | 65-270° | 60 | N/A | N/A | N/A | N/A | M7285Q1008 | N/A | FALSE
[24 empty] | 36 | M130JGA-1 | M9185D1004 | N/A | N/A | N/A | ADJ | N/A | 24 | 50 | 65-270° | 60 | N/A | N/A | N/A | N/A | M9185A1018 | N/A | FALSE
[24 empty] | 37 | M130JGB-1 | M9185D1004 | N/A | 220736A | N/A | ADJ | N/A | 24 | 50 | 65-270° | 60 | 1 | N/A | N/A | N/A | M9185E1019 | N/A | FALSE
[24 empty] | 38 | M130QGA-1 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | NDR | N/A | FALSE
[24 empty] | 39 | M140AAA-1 | M6184D1035 | N/A | N/A | N/A | ADJ | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | NDR | N/A | FALSE
[24 empty] | 40 | M140AGA-1 | M6184D1035 | N/A | N/A | N/A | ADJ | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | NDR | N/A | FALSE
[24 empty] | 41 | M140GGA-1 | M9174D1007 | N/A | N/A | Q7230A1005 | ADJ | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | NDR | Select signal range | FALSE
[24 empty] | 42 | M140JAA-1 | M9174D1007 | 50017460-003 | N/A | N/A | ADJ | N/A | 120 | 70 | 65-270° | 60 | N/A | N/A | N/A | N/A | M9174D1007 | N/A | FALSE
[24 empty] | 43 | M140JGA-1 | M9174D1007 | N/A | N/A | N/A | ADJ | N/A | 24 | 70 | 65-270° | 60 | N/A | N/A | N/A | N/A | M9174D1007 | N/A | FALSE
[24 empty] | 44 | M150AGA-1 | M6184D1035 | N/A | N/A | N/A | ADJ | N/A | 24 | 150 | 65-270° | 60 | N/A | N/A | N/A | N/A | M6184D1035 | N/A | FALSE
[24 empty] | 45 | M150AGB-1 | M6184D1035 | N/A | 220736A | N/A | ADJ | N/A | 24 | 150 | 65-270° | 60 | 1 | N/A | N/A | N/A | M6184F1017 | N/A | FALSE
[24 empty] | 46 | M150GGA-1 | M9184D1021 | N/A | N/A | Q7230A1005 | ADJ | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | NDR | Select signal range | FALSE
[24 empty] | 47 | M150JGA-1 | M9184D1021 | N/A | N/A | N/A | ADJ | N/A | 24 | 150 | 65-270° | 60 | N/A | N/A | N/A | N/A | M9184A1019 | N/A | FALSE
[24 empty] | 48 | M150JGB-1 | M9184D1021 | N/A | 220736A | N/A | ADJ | N/A | 24 | 150 | 65-270° | 60 | 1 | N/A | N/A | N/A | M9184F1034 | N/A | FALSE
[24 empty] | 49 | M150JGC-1 | M9184D1021 | N/A | 220736B | N/A | ADJ | N/A | 24 | 150 | 65-270° | 60 | 2 | N/A | N/A | N/A | M9184F1034 | N/A | FALSE
[24 empty] | 50 | M150QGA-1 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 150 | 65-270° | 60 | N/A | N/A | N/A | N/A | M7284q1009 | N/A | FALSE
[24 empty] | 51 | M204A1001 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 37 | 180 | 15 | N/A | N/A | N/A | Series 20 | M6184D1001 | Unidirectional stroke | FALSE
[24 empty] | 52 | M204A1019 | M6184D1035 | N/A | N/A | N/A | 160° | N/A | 24 | 54 | 180 | 30 | N/A | N/A | N/A | Series 20 | M6184D1001 | Unidirectional stroke | FALSE
[24 empty] | 53 | M204A1027 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 54 | 30 | 54 | N/A | N/A | N/A | Series 20 | NDR | Unidirectional stroke | FALSE
[24 empty] | 54 | M204A1035 | M6184D1035 | N/A | N/A | N/A | 160° | N/A | 24 | 108 | 180 | 60 | N/A | N/A | N/A | Series 20 | M6184D1035 | Unidirectional stroke | FALSE
[24 empty] | 55 | M204A1043 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 108 | 180 | 60 | N/A | N/A | N/A | Series 20 | NDR | Unidirectional stroke | FALSE
[24 empty] | 56 | M204A1050 | M6184D1035 | N/A | N/A | N/A | 160° | N/A | 24 | 108 | 180 | 240 | N/A | N/A | N/A | Series 20 | M6194D1017 | Unidirectional stroke | FALSE
[24 empty] | 57 | M204A1068 | M6184D1035 | N/A | N/A | N/A | 160° | N/A | 24 | 108 | 180 | 60 | N/A | N/A | N/A | Series 20 | M6184D1035 | Unidirectional stroke | FALSE
[24 empty] | 58 | M204B1000 | M6184D1035 | N/A | N/A | N/A | 160° | N/A | 24 | 108 | 180 | 60 | N/A | N/A | N/A | Series 20 | M6184D1035 | Unidirectional stroke | FALSE
[24 empty] | 59 | M405A1004 | N/A | N/A | N/A | N/A | N/A | N/A | 120 | 94 | 60 | 25 | N/A | N/A | N/A | Series 40 | NDR | N/A | FALSE
[24 empty] | 60 | M405A1020 | N/A | N/A | N/A | N/A | N/A | N/A | 240 | 94 | 60 | 25 | N/A | N/A | N/A | Series 40 | NDR | N/A | FALSE
[24 empty] | 61 | M405B1003 | M8185D1006 | 50017460-003 | N/A | N/A | 160° | N/A | 120 | 50 | 160 | 60 | N/A | N/A | N/A | Series 40 | M4185B1009 | N/A | FALSE
[24 empty] | 62 | M405B1011 | M8185D1006 | 50017460-001 | N/A | N/A | 160° | N/A | 208 | 50 | 160 | 60 | N/A | N/A | N/A | Series 40 | M4185B1058 + 220736A | N/A | FALSE
[24 empty] | 63 | M405B1029 | M8185D1006 | 50017460-001 | N/A | N/A | 160° | N/A | 240 | 50 | 160 | 60 | N/A | N/A | N/A | Series 40 | M4185B1058 + 220736A | N/A | FALSE
[24 empty] | 64 | M405B1037 | M8185D1006 | 50017460-003 | N/A | N/A | 160° | N/A | 120 | 50 | 160 | 60 | N/A | N/A | N/A | Series 40 | M4185A1001 | N/A | FALSE
[24 empty] | 65 | M405B1045 | M8185D1006 | 50017460-001 | N/A | N/A | 160° | N/A | 220 | 50 | 160 | 60 | N/A | N/A | N/A | Series 40 | NDR | N/A | FALSE
[24 empty] | 66 | M405B1052 | M8185D1006 | 50017460-003 | N/A | N/A | 90° | N/A | 120 | 50 | 60 | 60 | N/A | N/A | N/A | Series 40 | M4185B1058 + 220736A | Replaced Motor is 60° | FALSE
[24 empty] | 67 | M405B1086 | M8185D1006 | 50017460-001 | N/A | N/A | 90° | N/A | 220 | 50 | 60 | 60 | N/A | N/A | N/A | Series 40 | NDR | Replaced Motor is 60° | FALSE
[24 empty] | 68 | M405B1094 | M8185D1006 | 50017460-003 | N/A | N/A | 160° | N/A | 120 | 50 | 160 | 60 | N/A | N/A | N/A | Series 40 | M4185A1001 | N/A | FALSE
[24 empty] | 69 | M405B1102 | M8185D1006 | 50017460-003 | N/A | N/A | 160° | N/A | 120 | 50 | 160 | 60 | N/A | N/A | N/A | Series 40 | M4185A1001 | N/A | FALSE
[24 empty] | 70 | M405C1002 | M8185D1006 | 50017460-003 | N/A | N/A | 160° | N/A | 120 | 50 | 160 | 60 | N/A | N/A | N/A | Series 40 | M4185A1001 | N/A | FALSE
[24 empty] | 71 | M405C1010 | M8185D1006 | 50017460-001 | N/A | N/A | 160° | N/A | 208 | 50 | 160 | 60 | N/A | N/A | N/A | Series 40 | M4185B1058 + 220736A | N/A | FALSE
[24 empty] | 72 | M405C1028 | M8185D1006 | 50017460-001 | N/A | N/A | 160° | N/A | 220 | 50 | 160 | 60 | N/A | N/A | N/A | Series 40 | NDR | N/A | FALSE
[24 empty] | 73 | M405C1036 | M8185D1006 | 50017460-003 | N/A | N/A | 90° | N/A | 120 | 50 | 90 | 30 | N/A | N/A | N/A | Series 40 | M4185B1058 | N/A | FALSE
[24 empty] | 74 | M405C1044 | M8185D1006 | 50017460-001 | N/A | N/A | 90° | N/A | 208 | 50 | 90 | 30 | N/A | N/A | N/A | Series 40 | M4185B1058 | N/A | FALSE
[24 empty] | 75 | M405C1051 | M8185D1006 | 50017460-001 | N/A | N/A | 90° | N/A | 240 | 50 | 90 | 30 | N/A | N/A | N/A | Series 40 | M4185B1058 | N/A | FALSE
[24 empty] | 76 | M405C1069 | M8185D1006 | 50017460-001 | N/A | N/A | 160° | N/A | 240 | 50 | 160 | 60 | N/A | N/A | N/A | Series 40 | M4185B1058 + 220736A | N/A | FALSE
[24 empty] | 77 | M405D1001 | M8185D1006 | 50017460-003 | N/A | N/A | 160° | N/A | 120 | 50 | 160 | 60 | N/A | N/A | N/A | Series 40 | M4185B1009 | Use auxiliary end | FALSE
[24 empty] | 78 | M405D1019 | M8185D1006 | 50017460-001 | N/A | N/A | 160° | N/A | 208 | 50 | 160 | 60 | N/A | N/A | N/A | Series 40 | NDR | Use auxiliary end | FALSE
[24 empty] | 79 | M405D1027 | M8185D1006 | 50017460-001 | N/A | N/A | 160° | N/A | 240 | 50 | 160 | 60 | N/A | N/A | N/A | Series 40 | NDR | Use auxiliary end | FALSE
[24 empty] | 80 | M405D1035 | M8185D1006 | 50017460-001 | N/A | N/A | 160° | N/A | 220 | 27 | 160 | 60 | N/A | N/A | N/A | Series 40 | NDR | Use auxiliary end | FALSE
[24 empty] | 81 | M40AAA-1 | M9164D1009 | 50017460-003 | N/A | N/A | 90° | N/A | 120 | 35 | 90° | 34 | N/A | N/A | N/A | N/A | M9164A1005 | N/A | FALSE
[24 empty] | 82 | M40AAC-1 | M9164D1009 | 50017460-003 | 220736B | N/A | 90° | N/A | 120 | 35 | 90° | 34 | 2 | N/A | N/A | N/A | M9164C1068 | N/A | FALSE
[24 empty] | 83 | M40AGA-1 | M6184D1035 | N/A | N/A | N/A | 90° | N/A | 24 | 35 | 90° | 34 | N/A | N/A | N/A | N/A | M6184A1015 | N/A | FALSE
[24 empty] | 84 | M40AGC-1 | M9164D1009 | N/A | 220736B | N/A | 90° | N/A | 24 | 35 | 90° | 34 | 2 | N/A | N/A | N/A | NDR | N/A | FALSE
[24 empty] | 85 | M4172A1006 | M8185D1006 | 50017460-003 | N/A | N/A | 160 | N/A | 120 | 25 | 160 | 60 | N/A | 1 | N/A | Series 41 | M4185A1001 | N/A | TRUE
[24 empty] | 86 | M4172B1004 | M8185D1006 | 50017460-003 | 220736A | N/A | 160 | N/A | 120 | 25 | 160 | 60 | 1 | 1 | N/A | Series 41 | M4185B1009 | N/A | TRUE
[24 empty] | 87 | M4175D1015 | M4185B1058 | N/A | N/A | N/A | ADJ | N/A | 120 | 25 | 90/160 | 30/60 | N/A | 2 | N/A | Series 41 | NDR | N/A | TRUE
[24 empty] | 88 | M4175E1012 | M8185D1006 | 50017460-003 | 220736A | N/A | ADJ | N/A | 120 | 25 | 90/160 | 30/60 | 1 | 2 | N/A | Series 41 | NDR | N/A | TRUE
[24 empty] | 89 | M4182A1004 | M4185A1001 | 50017460-003 | N/A | N/A | 160 | N/A | 120 | 60 | 160 | 60 | N/A | 1 | N/A | Series 41 | M4185A1001 | N/A | TRUE
[24 empty] | 90 | M4182B1002 | M4185B1009 | N/A | 220736A | N/A | 160 | N/A | 120 | 60 | 160 | 60 | 1 | 1 | N/A | Series 41 | M4185B1009 | N/A | TRUE
[24 empty] | 91 | M4182B1010 | M8185D1006 | 50017460-001 | 220736A | N/A | 160 | N/A | MULTI | 60 | 160 | 60 | 1 | 1 | N/A | Series 41 | M4185B1058 + 220736A | N/A | TRUE
[24 empty] | 92 | M4182B1028 | M8185D1006 | 50017460-001 | 220736A | N/A | 160 | N/A | 220 | 60 | 160 | 60 | 1 | 1 | N/A | Series 41 | NDR | N/A | TRUE
[24 empty] | 93 | M4182B1036 | M4185B1009 | N/A | 220736A | N/A | 90 | N/A | 120 | 60 | 90 | 30 | 1 | 1 | N/A | Series 41 | M4185B1058 | N/A | TRUE
[24 empty] | 94 | M4182B1044 | M4185B1058 | N/A | 220736A | N/A | 90 | N/A | MULTI | 60 | 90 | 30 | 1 | 1 | N/A | Series 41 | M4185B1058 | N/A | TRUE
[24 empty] | 95 | M4182B1051 | M4185B1058 | N/A | 220736A | 4074ERU | 90 | N/A | 120 | 60 | 90 | 30 | 1 | 1 | N/A | Series 41 | M4185B1058 | Includes weatherproof kit | TRUE
[24 empty] | 96 | M4182B1069 | M8185D1006 | 50017460-003 | 220736A | 4074ERU | 160 | N/A | 120 | 60 | 160 | 60 | 1 | 1 | N/A | Series 41 | M4185B1009 | Includes weatherproof kit | TRUE
[24 empty] | 97 | M4185A1001 | N/A | N/A | N/A | N/A | 160 | N/A | 120 | 60 | 160 | 60 | N/A | 2 | N/A | Series 41 | N/A | N/A | TRUE
[24 empty] | 98 | M4185A1019 | N/A | N/A | N/A | N/A | N/A | N/A | 120 | 60 | 180 | 67 | N/A | 2 | N/A | Series 41 | NDR | N/A | TRUE
[24 empty] | 99 | M4185A1027 | M8185D1006 | 50017460-003 | N/A | N/A | 160 | N/A | 120 | 60 | 160 | 60 | N/A | 2 | N/A | Series 41 | M4185A1001 | N/A | TRUE
[24 empty] | 100 | M4185B1009 | N/A | N/A | N/A | N/A | 160 | N/A | 120 | 60 | 160 | 60 | 1 | 2 | N/A | Series 41 | N/A | N/A | TRUE
[24 empty] | 101 | M4185B1017 | M4185B1058 | N/A | 220736A | N/A | 160 | N/A | MULTI | 60 | 160 | 60 | 1 | 2 | N/A | Series 41 | M4185B1058 + 220736A | N/A | TRUE
[24 empty] | 102 | M4185B1025 | M8185D1006 | 50017460-001 | 220736A | N/A | 160 | N/A | 220 | 60 | 160 | 60 | 1 | 2 | N/A | Series 41 | NDR | N/A | TRUE
[24 empty] | 103 | M4185B1033 | M4185B1009 | N/A | 220736A | N/A | 160 | N/A | 120 | 60 | 160 | 60 | 1 | 2 | N/A | Series 41 | M4185B1009 | N/A | TRUE
[24 empty] | 104 | M4185B1041 | M8185D1006 | 50017460-001 | 220736A | N/A | 160 | N/A | MULTI | 60 | 160 | 60 | 1 | 2 | N/A | Series 41 | M4185B1058 + 220736A | N/A | TRUE
[24 empty] | 105 | M4185B1058 | N/A | N/A | N/A | N/A | 90 | N/A | MULTI | 60 | 90 | 30 | 1 | 2 | N/A | Series 41 | N/A | N/A | TRUE
[24 empty] | 106 | M4185B1066 | M8185D1006 | 50017460-003 | 220736A | N/A | 90 | N/A | 120 | 60 | 90 | 30 | 1 | 2 | N/A | Series 41 | M4185B1058 | N/A | TRUE
[24 empty] | 107 | M4185B1074 | M8185D1006 | 50017460-001 | 220736A | N/A | 160 | N/A | 220 | 60 | 160 | 60 | 1 | 2 | N/A | Series 41 | NDR | N/A | TRUE
[24 empty] | 108 | M4185C1007 | N/A | N/A | N/A | N/A | 90 | N/A | 120 | 60 | 90 | 30 | 2 | 2 | N/A | Series 41 | NDR | N/A | TRUE
[24 empty] | 109 | M4185D1013 | M8185D1006 | 50017460-003 | N/A | N/A | ADJ | N/A | 120 | 60 | 90/160 | 30 | N/A | 2 | N/A | Series 41 | NDR | N/A | TRUE
[24 empty] | 110 | M4185E1010 | M8185D1006 | 50017460-003 | 220736A | N/A | ADJ | 120 | 120 | 60 | 90/160 | 30 | 1 | 2 | N/A | Series 41 | NDR | N/A | TRUE
[24 empty] | 111 | M4185E4006 | N/A | N/A | N/A | N/A | ADJ | 120 | MULTI | 60 | 90/160 | 30/60 | 1 | 2 | YES | Series 41 | NDR | Canada Tradeline | TRUE
[24 empty] | 112 | M4185E4014 | N/A | N/A | N/A | N/A | ADJ | 120 | 120 | 60 | 90/160 | 30/60 | 1 | 2 | YES | Series 41 | NDR | Canada Tradeline | TRUE
[24 empty] | 113 | M4186H1005 | M8185D1006 | 50017460-003 | 220736A | N/A | 160 | N/A | 120 | 60 | 160 | 60 | 1 | 2 | YES | Series 41 | M4185B1009 | Use auxiliary shaft | TRUE
[24 empty] | 114 | M4186H4009 | M8185D1006 | 50017460-003 | 220736A | N/A | 160 | N/A | 120 | 60 | 160 | 60 | 1 | 2 | YES | Series 41 | NDR | Canada, use auxiliary shaft | TRUE
[24 empty] | 115 | M4186L4000 | M8185D1006 | 50017460-003 | 220736A | N/A | ADJ | N/A | 120 | 60 | 90/160 | 30/60 | 1 | 2 | YES | Series 41 | NDR | Canada, use auxiliary shaft | TRUE
[24 empty] | 116 | M436A1009 | N/A | N/A | N/A | N/A | N/A | N/A | 120 | 20 | 75° | 30 | 1 | N/A | N/A | Series 40 | M436A1116 | N/A | FALSE
[24 empty] | 117 | M436A1017 | N/A | N/A | N/A | N/A | N/A | N/A | 120 | 20 | 75° | 30 | 1 | N/A | N/A | Series 40 | M436A1116 | N/A | FALSE
[24 empty] | 118 | M436A1025 | N/A | N/A | N/A | N/A | N/A | N/A | 240 | 20 | 75° | 30 | 1 | N/A | N/A | Series 40 | M436A1124 | N/A | FALSE
[24 empty] | 119 | M436A1033 | N/A | N/A | N/A | N/A | N/A | N/A | 240 | 20 | 75° | 30 | 1 | N/A | N/A | Series 40 | M436A1124 | N/A | FALSE
[24 empty] | 120 | M436A1041 | N/A | N/A | N/A | N/A | N/A | N/A | 120 | 20 | 75° | 30 | 1 | N/A | N/A | Series 40 | M436A1116 | N/A | FALSE
[24 empty] | 121 | M436A1058 | N/A | N/A | N/A | N/A | N/A | N/A | 240 | 20 | 75° | 30 | 1 | N/A | N/A | Series 40 | M436A1124 | N/A | FALSE
[24 empty] | 122 | M436A1066 | N/A | N/A | N/A | N/A | N/A | N/A | 240 | 20 | 75° | 50 | 1 | N/A | N/A | Series 40 | M436A1124 | N/A | FALSE
[24 empty] | 123 | M436A1074 | N/A | N/A | N/A | N/A | N/A | N/A | 220 | 20 | 75° | 50 | 1 | N/A | N/A | Series 40 | M436A1140 | N/A | FALSE
[24 empty] | 124 | M436A1082 | N/A | N/A | N/A | N/A | N/A | N/A | 120 | 20 | 75° | 30 | 1 | N/A | N/A | Series 40 | M436A1116 | N/A | FALSE
[24 empty] | 125 | M436A1090 | N/A | N/A | N/A | N/A | N/A | N/A | 120 | 20 | 75° | 30 | 1 | N/A | N/A | Series 40 | M436A1124 | N/A | FALSE
[24 empty] | 126 | M436A1108 | N/A | N/A | N/A | N/A | N/A | N/A | 240 | 20 | 75° | 30 | 1 | N/A | N/A | Series 40 | M436A1124 | N/A | FALSE
[24 empty] | 127 | M436A1116 | N/A | N/A | N/A | N/A | N/A | N/A | 120 | 20 | 75° | 30 | 1 | N/A | N/A | Series 40 | M436A1116 | N/A | FALSE
[24 empty] | 128 | M436A1124 | N/A | N/A | N/A | N/A | N/A | N/A | 240 | 20 | 75° | 30 | 1 | N/A | N/A | Series 40 | M436A1124 | N/A | FALSE
[24 empty] | 129 | M436A1132 | N/A | N/A | N/A | N/A | N/A | N/A | 240 | 20 | 75° | 50 | 1 | N/A | N/A | Series 40 | M436A1124 | N/A | FALSE
[24 empty] | 130 | M436A1140 | N/A | N/A | N/A | N/A | N/A | N/A | 220 | 20 | 75° | 50 | 1 | N/A | N/A | Series 40 | M436A1124 | N/A | FALSE
[24 empty] | 131 | M436A1157 | N/A | N/A | N/A | N/A | N/A | N/A | 120 | 20 | 75° | 30 | 1 | N/A | N/A | Series 40 | M436A1116 | N/A | FALSE
[24 empty] | 132 | M436A1165 | N/A | N/A | N/A | N/A | N/A | N/A | 120 | 20 | 75° | 30 | 1 | N/A | N/A | Series 40 | M436A1116 | N/A | FALSE
[24 empty] | 133 | M436A1173 | N/A | N/A | N/A | N/A | N/A | N/A | 240 | 20 | 75° | 40 | 1 | N/A | N/A | Series 40 | M436A1124 | N/A | FALSE
[24 empty] | 134 | M445A1000 | M8185D1006 | 50017460-003 | 220736A | N/A | 160° | N/A | 120 | 50 | 160 | 60 | 1 | N/A | N/A | Series 40 | M4185B1009 | N/A | FALSE
[24 empty] | 135 | M445A1018 | M8185D1006 | 50017460-003 | 220736A | N/A | 160° | N/A | 120 | 50 | 160 | 60 | 1 | N/A | N/A | Series 40 | M4185B1009 | N/A | FALSE
[24 empty] | 136 | M445A1026 | M8185D1006 | 50017460-001 | 220736A | N/A | 160° | N/A | 208 | 50 | 160 | 60 | 1 | N/A | N/A | Series 40 | M4185B1058 + 220736A | N/A | FALSE
[24 empty] | 137 | M445A1034 | M8185D1006 | 50017460-001 | 220736A | N/A | 160° | N/A | 208 | 50 | 160 | 60 | 1 | N/A | N/A | Series 40 | M4185B1058 + 220736A | N/A | FALSE
[24 empty] | 138 | M445A1042 | M8185D1006 | 50017460-001 | 220736A | N/A | 160° | N/A | 208/240 | 50 | 160 | 60 | 1 | N/A | N/A | Series 40 | M4185B1058 + 220736A | N/A | FALSE
[24 empty] | 139 | M445A1059 | M8185D1006 | 50017460-001 | 220736A | N/A | 160° | N/A | 240 | 50 | 160 | 60 | 1 | N/A | N/A | Series 40 | M4185B1058 + 220736A | N/A | FALSE
[24 empty] | 140 | M445A1067 | M8185D1006 | 50017460-001 | 220736A | N/A | 160° | N/A | 220 | 50 | 160 | 60 | 1 | N/A | N/A | Series 40 | NDR | N/A | FALSE
[24 empty] | 141 | M445A1075 | M8185D1006 | 50017460-003 | 220736A | N/A | 90° | N/A | 120 | 50 | 60 | 25 | 1 | N/A | N/A | Series 40 | M4185B1058 | N/A | FALSE
[24 empty] | 142 | M445A1091 | M8185D1006 | 50017460-003 | 220736A | N/A | 160° | N/A | 120 | 50 | 160 | 60 | 1 | N/A | N/A | Series 40 | M4185B1009 | N/A | FALSE
[24 empty] | 143 | M445A1109 | M8185D1006 | 50017460-003 | 220736A | N/A | 160° | N/A | 120 | 50 | 160 | 60 | 1 | N/A | N/A | Series 40 | M4185B1009 | N/A | FALSE
[24 empty] | 144 | M445A1117 | M8185D1006 | 50017460-003 | 220736A | N/A | 90° | N/A | 120 | 50 | 90 | 30 | 1 | N/A | N/A | Series 40 | M4185B1058 | N/A | FALSE
[24 empty] | 145 | M445A1125 | M8185D1006 | 50017460-003 | 220736A | N/A | 90° | N/A | 120 | 50 | 90 | 15 | 1 | N/A | N/A | Series 40 | M4185B1058 | N/A | FALSE
[24 empty] | 146 | M445A4004 | M8185D1006 | 50017460-003 | 220736A | N/A | ADJ | 120° | 120 | 50 | 90/160 | 30/60 | 1 | N/A | N/A | Series 40 | NDR | N/A | FALSE
[24 empty] | 147 | M445C1008 | M8185D1006 | 50017460-003 | 220736A | N/A | 160° | N/A | 120 | 50 | 160 | 60 | 1 | N/A | N/A | Series 40 | M4185B1009 | N/A | FALSE
[24 empty] | 148 | M445C1016 | M8185D1006 | 50017460-003 | 220736A | N/A | 160° | 155° | 120 | 50 | 160 | 60 | 1 | N/A | N/A | Series 40 | M4185B1009 | N/A | FALSE
[24 empty] | 149 | M445C1024 | M8185D1006 | 50017460-003 | 220736A | N/A | 160° | N/A | 120 | 50 | 160 | 60 | 1 | N/A | N/A | Series 40 | M4185B1009 | N/A | FALSE
[24 empty] | 150 | M445D1007 | M8185D1006 | 50017460-003 | N/A | N/A | 160° | N/A | 120 | 50 | 160 | 60 | N/A | N/A | N/A | Series 40 | M4185A1001 | N/A | FALSE
[24 empty] | 151 | M445D1015 | M8185D1006 | 50017460-003 | N/A | N/A | 90° | N/A | 120 | 50 | 90 | 30 | N/A | N/A | N/A | Series 40 | M4185B1058 | N/A | FALSE
[24 empty] | 152 | M445D1023 | M8185D1006 | 50017460-001 | N/A | N/A | 160° | N/A | 220 | 50 | 160 | 60 | N/A | N/A | N/A | Series 40 | NDR | N/A | FALSE
[24 empty] | 153 | M445D1031 | M8185D1006 | 50017460-001 | N/A | N/A | 160° | N/A | 240 | 50 | 160 | 60 | N/A | N/A | N/A | Series 40 | M4185B1058 + 220736A | N/A | FALSE
[24 empty] | 154 | M445D1049 | M8185D1006 | 50017460-003 | N/A | N/A | 160° | N/A | 120 | 50 | 180 | 67 | N/A | N/A | N/A | Series 40 | M4185A1001 | N/A | FALSE
[24 empty] | 155 | M445D1056 | M8185D1006 | 50017460-003 | N/A | N/A | 160° | N/A | 120 | 50 | 160 | 60 | N/A | N/A | N/A | Series 40 | M4185A1001 | N/A | FALSE
[24 empty] | 156 | M465A1008 | M8185D1006 | 50017460-003 | N/A | N/A | 160° | N/A | 120 | 25 | 160 | 40 | N/A | N/A | N/A | Series 40 | M4185B1009 | N/A | FALSE
[24 empty] | 157 | M465B1007 | M8185D1006 | 50017460-003 | 220736B | N/A | 160° | N/A | 120 | 50 | 160 | 60 | 2 | N/A | N/A | Series 40 | M4185A1001 | N/A | FALSE
[24 empty] | 158 | M604A1002 | M6184D1035 | 50017460-003 | N/A | N/A | N/A | N/A | 120 | 75 | 360 | 30 | N/A | N/A | N/A | Series 61 | M6184A1023 | Tradeline is 90°/160° | FALSE
[24 empty] | 159 | M604A1028 | M6184D1035 | 50017460-001 | N/A | N/A | N/A | N/A | 240 | 40 | 360 | 60 | N/A | N/A | N/A | Series 61 | NDR | Tradeline is 90°/160° | FALSE
[24 empty] | 160 | M604A1036 | M6184D1035 | 50017460-001 | N/A | N/A | N/A | N/A | 208 | 54 | 360 | 30 | N/A | N/A | N/A | Series 61 | NDR | Tradeline is 90°/160° | FALSE
[24 empty] | 161 | M604A1051 | N/A | N/A | N/A | N/A | N/A | N/A | 240 | 40 | 180 | 15 | N/A | N/A | N/A | Series 61 | NDR | N/A | FALSE
[24 empty] | 162 | M604A1069 | M6184D1035 | 50017460-003 | N/A | N/A | N/A | N/A | 120 | 40 | 360 | 60 | N/A | N/A | N/A | Series 61 | NDR | Tradeline is 90°/160° | FALSE
[24 empty] | 163 | M604A1077 | M6184D1035 | 50017460-003 | N/A | N/A | N/A | N/A | 120 | 75 | 360 | 15 | N/A | N/A | N/A | Series 61 | NDR | Tradeline is 90°/160° | FALSE
[24 empty] | 164 | M604B1001 | M6184D1035 | 50017460-003 | N/A | N/A | 160° | N/A | 120 | 37 | 180 | 15 | N/A | N/A | N/A | Series 61 | M6184A1023 | Change control circuit to 24 Vac | FALSE
[24 empty] | 165 | M604B1019 | M6184D1035 | 50017460-001 | N/A | N/A | 160° | N/A | 240 | 37 | 180 | 30 | N/A | N/A | N/A | Series 61 | NDR | Change control circuit to 24 Vac | FALSE
[24 empty] | 166 | M604B1027 | M6184D1035 | 50017460-003 | N/A | N/A | 160° | N/A | 120 | 75 | 180 | 30 | N/A | N/A | N/A | Series 61 | M6184A1023 | Change control circuit to 24 Vac | FALSE
[24 empty] | 167 | M604B1035 | M6184D1035 | 50017460-001 | N/A | N/A | 160° | N/A | 208 | 54 | 180 | 30 | N/A | N/A | N/A | Series 61 | NDR | Change control circuit to 24 Vac | FALSE
[24 empty] | 168 | M604B1043 | M6184D1035 | 50017460-001 | N/A | N/A | 160° | N/A | 240 | 75 | 180 | 30 | N/A | N/A | N/A | Series 61 | NDR | Change control circuit to 24 Vac | FALSE
[24 empty] | 169 | M604B1050 | N/A | N/A | N/A | N/A | N/A | N/A | 120 | 54 | 180 | 30 | N/A | N/A | N/A | Series 61 | NDR | N/A | FALSE
[24 empty] | 170 | M604B1068 | M6184D1035 | 50017460-003 | N/A | N/A | 160° | N/A | 120 | 54 | 180 | 30 | N/A | N/A | N/A | Series 61 | M6184A1023 | Change control circuit to 24 Vac | FALSE
[24 empty] | 171 | M604B1076 | M6184D1035 | 50017460-001 | N/A | N/A | 160° | N/A | 220 | 54 | 180 | 30 | N/A | N/A | N/A | Series 61 | NDR | Change control circuit to 24 Vac | FALSE
[24 empty] | 172 | M604C1059 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 108 | 160 | 60 | N/A | N/A | N/A | Series 61 | NDR | N/A | FALSE
[24 empty] | 173 | M604C1083 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 150 | 160 | 120 | N/A | N/A | N/A | Series 61 | NDR | N/A | FALSE
[24 empty] | 174 | M604D1009 | M6184D1035 | 50017460-001 | N/A | N/A | 160° | N/A | 220 | 85 | 180 | 60 | N/A | N/A | N/A | Series 61 | NDR | N/A | FALSE
[24 empty] | 175 | M604D1017 | M6184D1035 | 50017460-001 | N/A | N/A | 160° | N/A | 220 | 85 | 180 | 60 | N/A | N/A | N/A | Series 61 | NDR | N/A | FALSE
[24 empty] | 176 | M604E1008 | M6184D1035 | N/A | 220736A | N/A | ADJ | N/A | 24 | 150 | 90/160 | 30/60 | 1 | N/A | N/A | Series 61 | M6184F1014 | N/A | FALSE
[24 empty] | 177 | M604E1016 | M6184D1035 | N/A | 220736A | N/A | ADJ | N/A | 24 | 150 | 90/160 | 30/60 | 1 | N/A | N/A | Series 61 | M6184F1014 | N/A | FALSE
[24 empty] | 178 | M604E1024 | M6184D1035 | N/A | 220736A | N/A | ADJ | N/A | 24 | 150 | 90/160 | 30/60 | 1 | N/A | N/A | Series 61 | M6184F1014 | N/A | FALSE
[24 empty] | 179 | M6161A1004 | M6184A1023 | N/A | N/A | N/A | 90 | N/A | 120 | 35 | 90 | 30 | N/A | 1 | N/A | Series 61 | M6184A1015 | N/A | TRUE
[24 empty] | 180 | M6161B1002 | M6184D1035 | 50017460-003 | 220736A | N/A | 90 | N/A | 120 | 35 | 90 | 30 | 1 | 1 | N/A | Series 61 | NDR | N/A | TRUE
[24 empty] | 181 | M6174A1009 | M6184D1035 | N/A | N/A | N/A | 160 | N/A | 24 | 75 | 160 | 60 | N/A | 2 | N/A | Series 61 | NDR | Includes auxiliary switch cams | TRUE
[24 empty] | 182 | M6174D1003 | M6184D1035 | 50017460-003 | N/A | N/A | ADJ | N/A | 120 | 75 | 90/160 | 30/60 | N/A | 2 | N/A | Series 61 | M6184D1035 | N/A | TRUE
[24 empty] | 183 | M6181A1000 | M6184D1035 | N/A | N/A | N/A | 160 | N/A | 24 | 150 | 160 | 60 | N/A | 1 | N/A | Series 61 | NDR | Less junction box | TRUE
[24 empty] | 184 | M6181A1018 | M6184A1015 | N/A | N/A | N/A | 160 | N/A | 24 | 150 | 160 | 60 | N/A | 1 | N/A | Series 61 | NDR | N/A | TRUE
[24 empty] | 185 | M6181A1026 | M6184D1035 | N/A | N/A | N/A | 90 | N/A | 24 | 150 | 90 | 30 | N/A | 1 | N/A | Series 61 | M6184A1015 | N/A | TRUE
[24 empty] | 186 | M6181A1034 | M6184A1023 | N/A | N/A | N/A | 160 | N/A | 120 | 75 | 160 | 30 | N/A | 1 | N/A | Series 61 | M6184A1023 | N/A | TRUE
[24 empty] | 187 | M6181A1042 | M6184D1035 | 50017460-003 | N/A | N/A | 160 | N/A | 120 | 150 | 160 | 60 | N/A | 1 | N/A | Series 61 | NDR | N/A | TRUE
[24 empty] | 188 | M6181A1059 | M6184D1035 | N/A | N/A | N/A | 160 | N/A | 24 | 150 | 160 | 60 | N/A | 1 | N/A | Series 61 | NDR | Carrier | TRUE
[24 empty] | 189 | M6181D1004 | M6184D1035 | N/A | N/A | N/A | ADJ | N/A | 24 | 75 | 90/160 | 15/30 | N/A | 1 | N/A | Series 61 | M6184D1001 | N/A | TRUE
[24 empty] | 190 | M6181F1009 | M6184F1014 | N/A | N/A | N/A | ADJ | N/A | 24 | 150 | 90/160 | 30/60 | 2 | 1 | N/A | Series 61 | M6184F1014 | N/A | TRUE
[24 empty] | 191 | M6181F1017 | M6184D1035 | 50017460-001 | 220736B | N/A | ADJ | 70 & 70 | MULTI | 150 | 90/160 | 30/60 | 2 | 1 | N/A | Series 61 | M6184F1014 | N/A | TRUE
[24 empty] | 192 | M6182D1003 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 60 | 90/160 | 15/60 | N/A | 1 | N/A | Series 61 | NDR | Carrier | TRUE
[24 empty] | 193 | M6182D1011 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 60 | 90/160 | SELECT | N/A | 1 | N/A | Series 61 | NDR | Carrier | TRUE
[24 empty] | 194 | M6182F1008 | N/A | N/A | N/A | N/A | N/A | 12 & 40 | 24 | 60 | 90/160 | 15/60 | 2 | 1 | N/A | Series 61 | NDR | Carrier | TRUE
[24 empty] | 195 | M6182F1016 | M6285A1005 | N/A | N/A | N/A | N/A | N/A | 24 | 60 | 90/160 | 30/60 | 2 | 1 | N/A | Series 61 | NDR | Includes weatherproof kit | TRUE
[24 empty] | 196 | M6184A1007 | M6184D1035 | N/A | N/A | N/A | 160 | N/A | 24 | 150 | 160 | 60 | N/A | 2 | N/A | Series 61 | NDR | N/A | TRUE
[24 empty] | 197 | M6184A1015 | N/A | N/A | N/A | N/A | 90 | N/A | 24 | 150 | 90 | 30 | N/A | 2 | N/A | Series 61 | N/A | N/A | TRUE
[24 empty] | 198 | M6184A1023 | N/A | N/A | N/A | N/A | 160 | N/A | 120 | 75 | 160 | 30 | N/A | 2 | N/A | Series 61 | N/A | N/A | TRUE
[24 empty] | 199 | M6184A1031 | M6184D1035 | N/A | N/A | N/A | 160 | N/A | 24 | 150 | 160 | 60 | N/A | 2 | N/A | Series 61 | NDR | Carrier | TRUE
[24 empty] | 200 | M6184A1049 | M6184D1035 | 50017460-003 | N/A | N/A | 160 | N/A | 120 | 75 | 160 | 30 | N/A | 2 | N/A | Series 61 | M6184A1023 | N/A | TRUE
[24 empty] | 201 | M6184A1056 | M6184D1035 | N/A | N/A | N/A | 90 | N/A | 24 | 150 | 90 | 30 | N/A | 2 | N/A | Series 61 | NDR | Trane | TRUE
[24 empty] | 202 | M6184B1005 | M6184D1035 | 50017460-003 | 220736A | N/A | 90 | 7 | 120 | 150 | 90 | 120 | 1 | 2 | YES | Series 61 | NDR | N/A | TRUE
[24 empty] | 203 | M6184B1013 | N/A | N/A | N/A | N/A | 90 | 7 | 120 | 150 | 90 | 120 | 1 | 2 | N/A | Series 61 | NDR | Trane | TRUE
[24 empty] | 204 | M6184B1021 | M6184D1035 | N/A | 220736A | N/A | 160 | N/A | 24 | 150 | 160 | 60 | 1 | 2 | N/A | Series 61 | M6184F1014 | N/A | TRUE
[24 empty] | 205 | M6184D1001 | N/A | N/A | N/A | N/A | ADJ | N/A | 24 | 75 | 90/160 | 15/30 | N/A | 2 | N/A | Series 61 | N/A | N/A | TRUE
[24 empty] | 206 | M6184D1035 | N/A | N/A | N/A | N/A | ADJ | N/A | 24 | 150 | 90/160 | 30/60 | N/A | 2 | YES | Series 61 | N/A | TRADELINE | TRUE
[24 empty] | 207 | M6184D1050 | M6184D1035 | N/A | N/A | N/A | ADJ | N/A | 24 | 75 | 90/160 | 15/30 | N/A | 2 | N/A | Series 61 | M6184D1001 | N/A | TRUE
[24 empty] | 208 | M6184D1068 | N/A | N/A | N/A | N/A | ADJ | N/A | 24 | 150 | 90/160 | 120/240 | N/A | 2 | N/A | Series 61 | N/A | N/A | TRUE
[24 empty] | 209 | M6184D1076 | M6184D1035 | N/A | N/A | N/A | ADJ | N/A | 24 | 150 | 90/160 | 30/60 | N/A | 2 | N/A | Series 61 | NDR | Trane | TRUE
[24 empty] | 210 | M6184F1006 | M6184D1035 | N/A | 220736B | N/A | ADJ | N/A | 24 | 150 | 90/160 | 30/60 | 2 | 2 | YES | Series 61 | M6184F1014 | N/A | TRUE
[24 empty] | 211 | M6184F1014 | N/A | N/A | 220736B | N/A | ADJ | N/A | 24 | 150 | 90/160 | 30/60 | 2 | 2 | N/A | Series 61 | N/A | N/A | TRUE
[24 empty] | 212 | M6185D1000 | M6285A1005 | N/A | N/A | N/A | N/A | N/A | 24 | 60 | 90/160 | 30/60 | N/A | 2 | N/A | Series 61 | NDR | N/A | TRUE
[24 empty] | 213 | M6191A1008 | M6194D1017 | 50017460-003 | N/A | N/A | 160 | N/A | 120 | 300 | 160 | 120 | N/A | 1 | N/A | Series 61 | NDR | N/A | TRUE
[24 empty] | 214 | M6191B1006 | M6194B1011 | N/A | 220736A | N/A | 90 | 7 | 24 | 300 | 90 | 60 | 1 | 1 | N/A | Series 61 | M6194B1011 | N/A | TRUE
[24 empty] | 215 | M6191D1002 | M6294D1008 | N/A | N/A | N/A | ADJ | N/A | 24 | 300 | 90/160 | 120/240 | N/A | 1 | N/A | Series 61 | M6194D1017 | N/A | TRUE
[24 empty] | 216 | M6191D1010 | M6194D1017 | 50017460-003 | N/A | N/A | ADJ | N/A | 120 | 300 | 90/160 | 120/240 | N/A | 1 | YES | Series 61 | NDR | York | TRUE
[24 empty] | 217 | M6194A1005 | N/A | N/A | N/A | N/A | 90 | N/A | 120 | 300 | 90 | 120 | N/A | 2 | N/A | Series 61 | NDR | N/A | TRUE
[24 empty] | 218 | M6194A1021 | M6194D1017 | N/A | N/A | N/A | 160 | N/A | 24 | 300 | 160 | 120 | N/A | 2 | N/A | Series 61 | NDR | With auxiliary switch cams | TRUE
[24 empty] | 219 | M6194B1003 | M6194D1017 | N/A | 220736A | N/A | 90 | 7 | 24 | 300 | 90 | 60 | 1 | 2 | YES | Series 61 | M6194B1011 | N/A | TRUE
[24 empty] | 220 | M6194B1011 | N/A | N/A | N/A | N/A | 90 | 7 | 24 | 300 | 90 | 60 | 1 | 2 | N/A | Series 61 | N/A | N/A | TRUE
[24 empty] | 221 | M6194B1029 | N/A | N/A | N.//A | N/A | 90 | 7 | 120 | 300 | 90 | 120 | 1 | 2 | N/A | Series 61 | N/A | Trane | TRUE
[24 empty] | 222 | M6194B1037 | M6194D1017 | 50017460-003 | 220736A | N/A | 90 | N/A | 120 | 300 | 90 | 120 | 1 | 2 | N/A | Series 61 | NDR | Trane | TRUE
[24 empty] | 223 | M6194B1045 | M6194D1017 | 50017460-003 | 220736A | N/A | 90 | N/A | 120 | 300 | 90 | 120 | 1 | 2 | N/A | Series 61 | M6194E1006 | N/A | TRUE
[24 empty] | 224 | M6194D1017 | N/A | N/A | N/A | N/A | ADJ | N/A | 24 | 300 | 90/160 | 120/240 | N/A | 2 | YES | Series 61 | N/A | TRADELINE | TRUE
[24 empty] | 225 | M6194D1025 | M6194D1017 | N/A | N/A | N/A | ADJ | N/A | 24 | 300 | 90/160 | 120/240 | N/A | 2 | N/A | Series 61 | NDR | Lennox | TRUE
[24 empty] | 226 | M6194D1033 | M6194D1017 | N/A | N/A | N/A | ADJ | N/A | 24 | 300 | 90/160 | 120/240 | N/A | 2 | N/A | Series 61 | NDR | York | TRUE
[24 empty] | 227 | M6194D1041 | M6194D1017 | N/A | N/A | 220741A | ADJ | N/A | 24 | 300 | 90/160 | 120/240 | N/A | 2 | N/A | Series 61 | NDR | Japan, includes 220741A | TRUE
[24 empty] | 228 | M6194D4003 | N/A | N/A | N/A | N/A | ADJ | N/A | 24 | 300 | 90/160 | 120/240 | N/A | 2 | YES | Series 61 | N/A | Canada Tradeline | TRUE
[24 empty] | 229 | M6194E1006 | N/A | N/A | 220736A | N/A | ADJ | N/A | 24 | 300 | 90/160 | 120/240 | 1 | 2 | N/A | Series 61 | N/A | N/A | TRUE
[24 empty] | 230 | M6194E1014 | M6194D1017 | N/A | 220736A | 4074ERU | ADJ | N/A | 24 | 300 | 90/160 | 120/240 | 1 | 2 | YES | Series 61 | M6194E1006 | Includes weatherproof kit | TRUE
[24 empty] | 231 | M6194F1004 | M6194D1017 | N/A | 220736B | N/A | ADJ | N/A | 24 | 300 | 90/160 | 120/240 | 2 | 2 | N/A | Series 61 | NDR | N/A | TRUE
[24 empty] | 232 | M6281A1009 | M6284D1000 | N/A | N/A | N/A | 160 | N/A | 24 | 150 | 160 | 60 | N/A | 1 | N/A | Series 62 | m6284a1055 | N/A | TRUE
[24 empty] | 233 | M6281F1008 | M6284D1000 | N/A | 220736B | N/A | ADJ | 7 & 57 | 24 | 150 | 90/160 | 30/60 | 2 | 1 | N/A | Series 62 | M6284F1013 | N/A | TRUE
[24 empty] | 234 | M6281F1016 | M6284F1062 | 50017460-003 | 220736B | N/A | ADJ | N/A | 120 | 150 | 90/160 | 30/60 | 2 | 1 | N/A | Series 62 | M6284F1013 | N/A | TRUE
[24 empty] | 235 | M6282A1008 | M6285A1005 | N/A | N/A | N/A | 160 | N/A | 24 | 60 | 160 | 60 | N/A | 1 | N/A | Series 62 | M6285A1005 | N/A | TRUE
[24 empty] | 236 | M6282A1016 | NDR | N/A | N/A | N/A | 90 | N/A | 120 | 60 | 90 | 30 | N/A | 1 | N/A | Series 62 | M6285A1005 and 50017460-003 | Trane | TRUE
[24 empty] | 237 | M6282A1024 | M6284A1005 | N/A | N/A | N/A | 90 | N/A | 24 | 25 | 90 | 60 | N/A | 1 | N/A | Series 62 | NDR | Trane | TRUE
[24 empty] | 238 | M6282A1032 | M6285A1005 | 50017460-003 | N/A | N/A | 160 | N/A | 120 | 60 | 160 | 60 | N/A | 1 | N/A | Series 62 | NDR | N/A | TRUE
[24 empty] | 239 | M6282B1006 | M6284A1005 | N/A | 220736A | N/A | 90 | N/A | 24 | 60 | 90 | 30 | 1 | 1 | N/A | Series 62 | NDR | N/A | TRUE
[24 empty] | 240 | M6282E1009 | N/A | N/A | N/A | N/A | N/A | 20 | 24 | 60 | 90/160 | 15/60 | 1 | 1 | N/A | Series 62 | NDR | Carrier | TRUE
[24 empty] | 241 | M6284A1006 | M6284D1000 | N/A | N/A | N/A | 160 | N/A | 24 | 150 | 160 | 60 | N/A | 2 | N/A | Series 62 | m6284a1055 | N/A | TRUE
[24 empty] | 242 | M6284A1014 | M6284D1000 | 50017460-003 | N/A | N/A | 160 | N/A | 120 | 150 | 160 | 60 | N/A | 2 | YES | Series 62 | m6284a1055 | N/A | TRUE
[24 empty] | 243 | M6284A1022 | M6284D1000 | 50017460-003 | N/A | N/A | 90 | N/A | 120 | 150 | 90 | 30 | N/A | 2 | YES | Series 62 | M6284A1055 | N/A | TRUE
[24 empty] | 244 | M6284A1030 | N/A | N/A | N/A | N/A | 160 | N/A | 24 | 150 | 160 | 60 | N/A | 2 | YES | Series 62 | NDR | Japan, includes 220741A | TRUE
[24 empty] | 245 | M6284A1048 | M6284A1055 | N/A | N/A | N/A | 160 | N/A | 120 | 150 | 160 | 60 | N/A | 2 | N/A | Series 62 | NDR | N/A | TRUE
[24 empty] | 246 | M6284A1055 | N/A | N/A | N/A | N/A | 90 | N/A | 120 | 150 | 90 | 30 | N/A | 2 | N/A | Series 62 | N/A | N/A | TRUE
[24 empty] | 247 | M6284A1063 | M6284D1000 | 50017460-003 | N/A | 220741A | 160 | N/A | 120 | 150 | 160 | 60 | N/A | 2 | N/A | Series 62 | M6284A1063 | Includes 220741A | TRUE
[24 empty] | 248 | M6284A1071 | N/A | N/A | N/A | N/A | 90 | N/A | 120 | 150 | 90 | 30 | N/A | 2 | N/A | Series 62 | N/A | Includes 220741A | TRUE
[24 empty] | 249 | M6284A1089 | N/A | N/A | N/A | N/A | 90 | N/A | 120 | 75 | 90 | 15 | N/A | 2 | N/A | Series 62 | NDR | Includes 220741A | TRUE
[24 empty] | 250 | M6284A1097 | N/A | N/A | N/A | N/A | 90 | N/A | 24 | 150 | 90 | 30 | N/A | 2 | N/A | Series 62 | N/A | N/A | TRUE
M6284A1113 | [23 empty] | 251 | M6284A1113 | M6284D1000 | 50017460-003 |  | 4074ERU | ADJ | N/A | 24 | 150 | 90/160 | 30/60 | N/A |  | N/A | Series 62 | M6284D1000 | WITH 50017460-003 AND 4074ERU Weather proof kit | TRUE
[24 empty] | 252 | M6284B1004 | N/A | N/A | N/A | N/A | 160 | 7 | 120 | 150 | 160 | 240 | 1 | 2 | N/A | Series 62 | NDR | Trane | TRUE
[24 empty] | 253 | M6284C1002 | M6284D1000 | N/A | 220736B | N/A | 90 | N/A | 24 | 150 | 90 | 30 | 2 | 2 | N/A | Series 62 | M6284F1013 | N/A | TRUE
[24 empty] | 254 | M6284C1010 | N/A | N/A | N/A | N/A | 90 | 42 & 48 | 24 | 150 | 90 | 30 | 2 | 2 | N/A | Series 62 | NDR | Includes 220741A | TRUE
[24 empty] | 255 | M6284C1028 | N/A | N/A | N./A | 220738A | 90 | N/A | 24 | 150 | 90 | 30 | 2 | 2 | YES | Series 62 | NDR | Japan, includes 220741A | TRUE
[24 empty] | 256 | M6284C1036 | M6284D1000 | 50017460-003 | 220736B | 4074ERU | 160 | N/A | 120 | 150 | 160 | 60 | 2 | 2 | N/A | Series 62 | NDR | Includes weatherproof kit | TRUE
[24 empty] | 257 | M6284C1044 | N/A | N/A | N/A | N/A | 90 | N/A | 120 | 150 | 90 | 30 | 2 | 2 | N/A | Series 62 | NDR | Includes weatherproof kit | TRUE
[24 empty] | 258 | M6284D1000 | N/A | N/A | N/A | N/A | ADJ | N/A | 24 | 150 | 90/160 | 30/60 | N/A | 2 | YES | Series 62 | N/A | TRADELINE | TRUE
[24 empty] | 259 | M6284D1026 | N/A | N/A | N/A | N/A | ADJ | N/A | 24 | 150 | 90/160 | 30/60 | N/A | 2 | N/A | Series 62 | NDR | Includes 220741A | TRUE
[24 empty] | 260 | M6284D4004 | N/A | N/A | N/A | N/A | ADJ | N/A | 24 | 150 | 90/160 | 30/60 | N/A | 2 | YES | Series 62 | N/A | Canada Tradeline | TRUE
[24 empty] | 261 | M6284F1005 | M6284D1000 | N/A | 220736B | N/A | ADJ | 7 & 57 | 24 | 150 | 90/160 | 30/60 | 2 | 2 | N/A | Series 62 | M6284F1013 | N/A | TRUE
[24 empty] | 262 | M6284F1013 | N/A | N/A | N/A | N/A | ADJ | N/A | 24 | 150 | 90/160 | 30/60 | 2 | 2 | N/A | Series 62 | N/A | N/A | TRUE
[24 empty] | 263 | M6284F1021 | M6284D1000 | 50017460-003 | 220736B | N/A | ADJ | N/A | 120 | 150 | 90/160 | 30/60 | 2 | 2 | YES | Series 62 | M6284F1013 | N/A | TRUE
[24 empty] | 264 | M6284F1039 | N/A | N/A | N/A | N/A | ADJ | N/A | 24 | 150 | 90/160 | 30/60 | 2 | 2 | YES | Series 62 | N/A | Japan, includes 220741A | TRUE
[24 empty] | 265 | M6284F1047 | M6284D1000 | 50017460-003 | 220736B | N/A | ADJ | N/A | 120 | 150 | 90/160 | 30/60 | 2 | 2 | N/A | Series 62 | M6284F1013 | N/A | TRUE
[24 empty] | 266 | M6284F1054 | M6284F1062 | N/A | N/A | N/A | ADJ | N/A | 220 | 150 | 90/160 | 30/60 | 2 | 2 | N/A | Series 62 | NDR | N/A | TRUE
[24 empty] | 267 | M6285A1005 | N/A | N/A | N/A | N/A | 160 | N/A | 24 | 60 | 160 | 60 | N/A | 2 | YES | Series 62 | N/A | TRADELINE | TRUE
[24 empty] | 268 | M6285A1013 | M6285A1005 | N/A | N/A | 220738A | 90 | N/A | 24 | 60 | 90 | 30 | N/A | 2 | YES | Series 62 | M6285A1005 | TRADELINE | TRUE
[24 empty] | 269 | M6285A1021 | M6284A1005 | 50017460-003 | N/A | N/A | 90 | N/A | 120 | 60 | 90 | 30 | N/A | 2 | N/A | Series 62 | NDR | N/A | TRUE
[24 empty] | 270 | M6285A1039 | N/A | N/A | N/A | N/A | 90 | N/A | 24 | 25 | 90 | 60 | N/A | 2 | N/A | Series 62 | NDR | Trane | TRUE
[24 empty] | 271 | M6285A1047 | N/A | N/A | N/A | N/A | 160 | N/A | 24 | 60 | 160 | 60 | N/A | 2 | YES | Series 62 | NDR | Japan, includes 220741A | TRUE
[24 empty] | 272 | M6285A1054 | N/A | N/A | N/A | N/A | 160 | N/A | 120 | 60 | 160 | 60 | N/A | 2 | N/A | Series 62 | NDR | Snyder General | TRUE
[24 empty] | 273 | M6285A4009 | N/A | N/A | N/A | N/A | 160 | N/A | 24 | 60 | 160 | 60 | N/A | 2 | YES | Series 62 | N/A | Canada Tradeline | TRUE
[24 empty] | 274 | M6285B1003 | M6284A1005 | N/A | 220736A | N/A | 90 | N/A | 24 | 60 | 90 | 30 | 1 | 2 | N/A | Series 62 | NDR | N/A | TRUE
[24 empty] | 275 | M6285C1001 | N/A | N/A | N/A | N/A | 160 | N/A | 24 | 60 | 160 | 60 | 2 | 2 | N/A | Series 62 | N/A | N/A | TRUE
[24 empty] | 276 | M6286G1001 | M6285A1005 | N/A | N/A | N/A | 160 | N/A | 24 | 60 | 160 | 60 | N/A | 2 | N/A | Series 62 | M6285A1005 | Use auxiliary shaft | TRUE
[24 empty] | 277 | M6286G1019 | M6285A1005 | 50017460-001 | N/A | N/A | 160 | N/A | 220 | 60 | 160 | 60 | N/A | 2 | N/A | Series 62 | NDR | Use auxiliary shaft | TRUE
[24 empty] | 278 | M6286G1027 | M6285A1005 | N/A | N/A | 220741A | 160 | N/A | 24 | 60 | 160 | 60 | N/A | 2 | YES | Series 62 | M6285A1005 | Japan, includes 220741A, use auxiliary shaft | TRUE
[24 empty] | 279 | M6294A1004 | M6294D1008 | 50017460-003 | N/A | N/A | 160 | N/A | 120 | 300 | 160 | 240 | N/A | 2 | N/A | Series 62 | NDR | N/A | TRUE
[24 empty] | 280 | M6294B1002 | M6294D1008 | N/A | 220736A | N/A | 160 | N/A | 24 | 300 | 160 | 240 | 1 | 2 | YES | Series 62 | NDR | N/A | TRUE
[24 empty] | 281 | M6294B1010 | M6294D1008 | 50017460-003 | 220736A | N/A | 160 | N/A | 120 | 300 | 160 | 240 | 1 | 2 | N/A | Series 62 | NDR | N/A | TRUE
[24 empty] | 282 | M6294B1028 | M6294D1008 | 50017460-003 | 220736A | N/A | 160 | 7 | 120 | 300 | 160 | 240 | 1 | 2 | N/A | Series 62 | NDR | Trane | TRUE
[24 empty] | 283 | M6294B1036 | N/A | N/A | N/A | N/A | 160 | N/A | 24 | 300 | 160 | 120 | 1 | 2 | N/A | Series 62 | NDR | N/A | TRUE
[24 empty] | 284 | M6294C1000 | M6294D1008 | 50017460-003 | 220736B | 220741A | 90 | N/A | 120 | 300 | 90 | 60 | 2 | 2 | N/A | Series 62 | NDR | Includes 220741A | TRUE
[24 empty] | 285 | M6294D1008 | N/A | N/A | N/A | N/A | ADJ | N/A | 24 | 300 | 90/160 | 120/240 | N/A | 2 | YES | Series 62 | N/A | TRADELINE | TRUE
[24 empty] | 286 | M634A1009 | M6184D1035 | N/A | N/A | N/A | 160° | N/A | 24 | 35 | 160 | 60 | N/A | N/A | N/A | Series 61 | M6184D1035 | N/A | FALSE
[24 empty] | 287 | M634B1008 | M6184D1035 | 50017460-003 | N/A | N/A | 160° | N/A | 120 | 35 | 160 | 60 | N/A | N/A | N/A | Series 61 | NDR | Change control circuit to 24 Vac | FALSE
[24 empty] | 288 | M634B1016 | M6184D1035 | 50017460-001 | N/A | N/A | 160° | N/A | 240 | 35 | 160 | 60 | N/A | N/A | N/A | Series 61 | NDR | Change control circuit to 24 Vac | FALSE
[24 empty] | 289 | M634C1007 | M6184D1035 | N/A | 220736B | N/A | 160° | N/A | 24 | 35 | 160 | 60 | 2 | N/A | N/A | Series 61 | M6184F1014 | N/A | FALSE
[24 empty] | 290 | M634C1015 | M6184D1035 | 50017460-003 | 220736B | N/A | 160° | N/A | 120 | 35 | 160 | 60 | 2 | N/A | N/A | Series 61 | M6184F1014 | N/A | FALSE
[24 empty] | 291 | M634C1023 | M6184D1035 | 50017460-001 | 220736B | N/A | 160° | N/A | 240 | 35 | 160 | 60 | 2 | N/A | N/A | Series 61 | M6184F1014 | N/A | FALSE
[24 empty] | 292 | M634C1031 | M6184D1035 | 50017460-001 | 220736B | N/A | 160° | N/A | 220 | 35 | 160 | 60 | 2 | N/A | N/A | Series 61 | M6184F1014 | N/A | FALSE
[24 empty] | 293 | M634C1049 | M6184D1035 | 50017460-003 | 220736B | N/A | 160° | N/A | 120 | 35 | 160 | 60 | 2 | N/A | N/A | Series 61 | M6184F1014 | N/A | FALSE
[24 empty] | 294 | M634C1056 | M6184D1035 | N/A | 220736B | N/A | 160° | N/A | 24 | 35 | 160 | 60 | 2 | N/A | N/A | Series 61 | M6184F1014 | N/A | FALSE
[24 empty] | 295 | M634C1064 | M6184D1035 | 50017460-001 | 220736B | N/A | 160° | N/A | 220 | 35 | 160 | 60 | 2 | N/A | N/A | Series 61 | M6184F1014 | N/A | FALSE
[24 empty] | 296 | M634C1072 | M6184D1035 | 50017460-003 | 220736B | N/A | 160° | N/A | 120 | 35 | 160 | 60 | 2 | N/A | N/A | Series 61 | M6184F1014 | N/A | FALSE
[24 empty] | 297 | M634C1080 | M6184D1035 | 50017460-001 | 220736B | N/A | 160° | N/A | 220 | 35 | 160 | 60 | 2 | N/A | N/A | Series 61 | M6184F1014 | N/A | FALSE
[24 empty] | 298 | M634C1098 | M6184D1035 | 50017460-001 | 220736B | N/A | 160° | N/A | 220 | 35 | 160 | 60 | 2 | N/A | N/A | Series 61 | M6184F1014 | N/A | FALSE
[24 empty] | 299 | M6410A1011 | N/A | N/A | N/A | N/A | N/A | N/A | 24 Vac | 40.5 lb | 0.25 inch | 150 s at 50 Hz, 125 s at 60 Hz | N/A | N/A | N/A | Spdt floating | N/A | N/A | TRUE
[24 empty] | 300 | M6410A1029 | N/A | N/A | N/A | N/A | N/A | N/A | 24 Vac | 40.5 lb | 0.25 inch | 150 s at 50 Hz, 125 s at 60 Hz | N/A | N/A | N/A | Spdt floating | N/A | N/A | TRUE
[24 empty] | 301 | M6414A1009 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 25 | 90° | 90 | 1 | N/A | N/A | SPDT Floating | NDR | N/A | FALSE
[24 empty] | 302 | M6415A1008 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 25 | 90° | 90 | 1 | N/A | N/A | SPDT Floating | M6415A1016 | N/A | FALSE
[24 empty] | 303 | M6415A1016 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 25 | 90° | 90 | 1 | N/A | N/A | SPDT Floating | M6415A1016 | N/A | FALSE
[24 empty] | 304 | M6415B1006 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 25 | 90° | 90 | N/A | N/A | N/A | SPDT Floating | M6415B1014 | N/A | FALSE
[24 empty] | 305 | M6415B1014 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 25 | 90° | 90 | N/A | N/A | N/A | SPDT Floating | M6415B1014 | N/A | FALSE
[24 empty] | 306 | M644A1008 | M6184D1035 | N/A | N/A | N/A | 160° | N/A | 24 | 150 | 160 | 60 | N/A | N/A | N/A | Series 61 | M6184D1035 | N/A | TRUE
[24 empty] | 307 | M644A1016 | M6184D1035 | N/A | N/A | N/A | 160° | N/A | 24 | 150 | 160 | 60 | N/A | N/A | N/A | Series 61 | M6184D1035 | N/A | FALSE
[24 empty] | 308 | M644A1024 | M6184D1035 | N/A | N/A | N/A | 90° | N/A | 24 | 150 | 90 | 30 | N/A | N/A | N/A | Series 61 | M6184A1015 | N/A | FALSE
[24 empty] | 309 | M644A1032 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 37 | 160 | 15 | N/A | N/A | N/A | Series 61 | NDR | N/A | FALSE
[24 empty] | 310 | M644A1107 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 37 | 335 | 15 | N/A | N/A | N/A | Series 61 | NDR | N/A | FALSE
[24 empty] | 311 | M644A1115 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 37 | 335 | 30 | N/A | N/A | N/A | Series 61 | NDR | N/A | FALSE
[24 empty] | 312 | M644A1149 | M6184D1035 | 50017460-001 | N/A | N/A | 160° | N/A | 220 | 150 | 160 | 60 | N/A | N/A | N/A | Series 61 | NDR | N/A | FALSE
[24 empty] | 313 | M644A1180 | M6184D1035 | N/A | N/A | N/A | 160° | N/A | 24 | 150 | 160 | 60 | N/A | N/A | N/A | Series 61 | M6184D1035 | N/A | FALSE
[24 empty] | 314 | M644B1007 | M6184D1035 | 50017460-003 | N/A | N/A | 160° | N/A | 120 | 75 | 160 | 30 | N/A | N/A | N/A | Series 61 | NDR | Change control circuit to 24 Vac | FALSE
[24 empty] | 315 | M644B1015 | N/A | N/A | N/A | N/A | N/A | N/A | 120 | 37 | 160 | 15 | N/A | N/A | N/A | Series 61 | NDR | N/A | FALSE
[24 empty] | 316 | M644B1031 | M6184D1035 | 50017460-003 | N/A | N/A | 90° | N/A | 120 | 150 | 90 | 120 | N/A | N/A | N/A | Series 61 | NDR | Change control circuit to 24 Vac | FALSE
[24 empty] | 317 | M644B1049 | M6184D1035 | 50017460-003 | N/A | N/A | 160° | N/A | 120 | 75 | 160 | 30 | N/A | N/A | N/A | Series 61 | M6184A1023 | Tradeline is 30/60 second timing | FALSE
[24 empty] | 318 | M644B1056 | M6194D1017 | 50017460-003 | N/A | N/A | 90° | N/A | 120 | 150 | 90 | 120 | N/A | N/A | N/A | Series 61 | NDR | N/A | FALSE
[24 empty] | 319 | M644C1006 | M6184D1035 | N/A | N/A | N/A | ADJ | N/A | 24 | 75 | 90/160 | 15/30 | N/A | N/A | N/A | Series 61 | M6184D1001 | Tradeline is 30/60 second timing | FALSE
[24 empty] | 320 | M644C1014 | M6194D1017 | N/A | N/A | N/A | ADJ | N/A | 24 | 150 | 90/160 | 120/240 | N/A | N/A | N/A | Series 61 | M6194D1017 | N/A | FALSE
[24 empty] | 321 | M644C1022 | M6184D1035 | 50017460-003 | N/A | N/A | ADJ | N/A | 120 | 150 | 90/160 | 120/240 | N/A | N/A | N/A | Series 61 | NDR | N/A | FALSE
[24 empty] | 322 | M644C1030 | M6194D1017 | N/A | N/A | N/A | ADJ | N/A | 24 | 150 | 90/160 | 120/240 | N/A | N/A | N/A | Series 61 | M6194D1017 | N/A | FALSE
[24 empty] | 323 | M644C1055 | M6194D1017 | N/A | N/A | N/A | ADJ | N/A | 24 | 150 | 90/160 | 120/240 | N/A | N/A | N/A | Series 61 | M6194D1017 | N/A | FALSE
[24 empty] | 324 | M644C1063 | M6184D1035 | 50017460-003 | N/A | N/A | ADJ | N/A | 120 | 150 | 90/160 | 120/240 | N/A | N/A | N/A | Series 61 | NDR | N/A | FALSE
[24 empty] | 325 | M644C1071 | M6194D1017 | N/A | N/A | N/A | ADJ | N/A | 24 | 150 | 90/160 | 120/240 | N/A | N/A | N/A | Series 61 | NDR | N/A | FALSE
[24 empty] | 326 | M644C4000 | M6194D1017 | N/A | N/A | N/A | ADJ | N/A | 24 | 150 | 90/160 | 120/240 | N/A | N/A | N/A | Series 61 | M6194D1017 | N/A | FALSE
[24 empty] | 327 | M644D1005 | M6184D1035 | N/A | 220736B | N/A | ADJ | N/A | 24 | 150 | 90/160 | 30/60 | 2 | N/A | N/A | Series 61 | M6184F1014 | N/A | FALSE
[24 empty] | 328 | M644D1013 | M6184D1035 | N/A | 220736B | N/A | ADJ | N/A | 24 | 150 | 90/160 | 30/60 | 2 | N/A | N/A | Series 61 | M6184F1014 | N/A | FALSE
[24 empty] | 329 | M644D1021 | M6184D1035 | N/A | 220736B | N/A | ADJ | N/A | 24 | 150 | 90/160 | 30/60 | 2 | N/A | N/A | Series 61 | M6184F1014 | N/A | FALSE
[24 empty] | 330 | M644D1039 | M6184D1035 | N/A | 220736B | N/A | ADJ | N/A | 24 | 150 | 90/160 | 30/60 | 2 | N/A | N/A | Series 61 | M6184F1014 | N/A | FALSE
[24 empty] | 331 | M644D1047 | M6194D1017 | N/A | 220736B | N/A | ADJ | N/A | 24 | 150 | 90/160 | 120/240 | 2 | N/A | N/A | Series 61 | NDR | N/A | FALSE
[24 empty] | 332 | M644E1004 | M6184D1035 | N/A | 220736A | N/A | ADJ | N/A | 24 | 150 | 90/160 | 30/60 | 1 | N/A | N/A | Series 61 | M6184F1014 | N/A | FALSE
[24 empty] | 333 | M644E1012 | M6194D1017 | N/A | 220736A | N/A | 90° | N/A | 24 | 150 | 90 | 60 | 1 | N/A | N/A | Series 61 | M6194B1011 | Tradeline is 30/60 second timing | FALSE
[24 empty] | 334 | M644E1020 | M6184D1035 | 50017460-003 | 220736A | N/A | ADJ | N/A | 120 | 75 | 90/160 | 15/30 | 1 | N/A | N/A | Series 61 | NDR | N/A | FALSE
[24 empty] | 335 | M644E1038 | M6184D1035 | N/A | 220736A | N/A | ADJ | N/A | 24 | 75 | 90/160 | 15/30 | 1 | N/A | N/A | Series 61 | M6184D1001 | N/A | FALSE
[24 empty] | 336 | M644E1053 | M6194D1017 | N/A | 220736A | N/A | ADJ | N/A | 24 | 300 | 90/160 | 120/240 | 1 | N/A | N/A | Series 61 | M6194E1006 | N/A | FALSE
[24 empty] | 337 | M644F1003 | M6184D1035 | 50017460-003 | N/A | N/A | 160° | N/A | 120 | 75 | 180 | 30 | N/A | N/A | N/A | Series 61 | M6184D1001 | Change control circuit to 24 Vac, Trane Special | FALSE
[24 empty] | 338 | M644L1006 | M6194D1017 | 50017460-003 | 220736A | N/A | 90° | N/A | 120 | 150 | 90 | 120 | 1 | N/A | N/A | Series 61 | NDR | N/A | FALSE
[24 empty] | 339 | M644L1014 | M6184D1035 | 50017460-003 | 220736A | N/A | 90° | N/A | 120 | 150 | 90 | 30 | 1 | N/A | N/A | Series 61 | M6184F1014 | N/A | FALSE
[24 empty] | 340 | M644L1022 | M6194D1017 | 50017460-003 | 220736A | N/A | 90° | N/A | 120 | 150 | 90 | 120 | 1 | N/A | N/A | Series 61 | NDR | N/A | FALSE
[24 empty] | 341 | M644L1030 | M6194D1017 | 50017460-003 | 220736A | N/A | 90° | 7° | 120 | 150 | 90 | 120 | 1 | N/A | N/A | Series 61 | NDR | N/A | FALSE
[24 empty] | 342 | M7161A1002 | M9164D1009 | 50017460-003 | N/A | Q7130A1006 | 90 | N/A | 120 | 35 | 90 | 30 | N/A | 1 | N/A | 6-9 Vdc | NDR | N/A | FALSE
[24 empty] | 343 | M7161B1000 | M9164D1009 | 50017460-003 | 220736A | Q7130A1006 | 160 | 20 | 120 | 35 | 160 | 60 | 1 | 1 | N/A | 6-9 Vdc | NDR | N/A | TRUE
[24 empty] | 344 | M7161B1018 | M9184D1021 | 50017460-001 | 220736A | Q7130A1006 | 160 | 20 | 120 | 35 | 160 | 60 | 1 | 1 | N/A | 6-9 Vdc | NDR | Trane | TRUE
[24 empty] | 345 | M7161G1009 | M9164D1009 | 50017460-003 | N/A | Q7130A1006 | 90 | N/A | 120 | 35 | 90 | 30 | N/A | 1 | N/A | 10.5-13.5 Vdc | M7164G1030 | N/A | TRUE
[24 empty] | 346 | M7161G1017 | M9184D1021 | 50017460-003 | N/A | Q7130A1006 | 90 | N/A | 120 | 35 | 90 | 30 | N/A | 1 | N/A | 4-7 Vdc | NDR | N/A | TRUE
[24 empty] | 347 | M7161G1025 | M9164D1009 | N/A | N/A | Q7130A1006 | 160 | N/A | 24 | 35 | 160 | 60 | N/A | 1 | N/A | 4-7 Vdc | NDR | N/A | TRUE
[24 empty] | 348 | M7164A1009 | M9164D1009 | N/A | N/A | Q7130A1006 | 160 | N/A | 24 | 35 | 160 | 60 | N/A | 2 | YES | 4-7 Vdc | NDR | N/A | TRUE
[24 empty] | 349 | M7164A1017 | N/A | N/A | N/A | N/A | 90 | N/A | 24 | 35 | 90 | 30 | N/A | 2 | N/A | 10.5-13.5 Vdc | N/A | N/A | TRUE
[24 empty] | 350 | M7164A1025 | M9164D1009 | N/A | N/A | Q7130A1006 | 90 | N/A | 24 | 35 | 90 | 30 | N/A | 2 | N/A | 10.5-13.5 Vdc | NDR | Lennox | TRUE
[24 empty] | 351 | M7164A1033 | M9164D1009 | N/A | N/A | Q7130A1006 | 160 | N/A | 24 | 35 | 160 | 60 | N/A | 2 | N/A | 10.5-13.5 Vdc | NDR | N/A | TRUE
[24 empty] | 352 | M7164A1041 | M9164D1009 | N/A | N/A | Q7130A1006 | 160 | N/A | 24 | 35 | 160 | 60 | N/A | 2 | N/A | 4-7 Vdc | NDR | N/A | TRUE
[24 empty] | 353 | M7164A1058 | M9164D1009 | 50017460-001 | N/A | Q7130A1006 | 90 | N/A | 24 | 35 | 90 | 30 | N/A | 2 | N/A | 10.5-13.5 Vdc | M7164A1017 | N/A | TRUE
[24 empty] | 354 | M7164B1007 | M9164D1009 | 50017460-003 | 220736A | Q7130A1006 | 160 | 20 | 120 | 35 | 160 | 60 | 1 | 2 | YES | 6-9 Vdc | NDR | N/A | TRUE
[24 empty] | 355 | M7164G1006 | M9164D1009 | 50017460-003 | N/A | Q7130A1006 | 90 | N/A | 120 | 35 | 90 | 30 | N/A | 2 | YES | 10.5-13.5 Vdc | M7164G1030 | N/A | TRUE
[24 empty] | 356 | M7164G1014 | M9164D1009 | 50017460-003 | N/A | Q7130A1006 | 90 | N/A | 120 | 35 | 90 | 30 | N/A | 2 | YES | 4-7 Vdc | NDR | N/A | TRUE
[24 empty] | 357 | M7164G1022 | M9164D1009 | N/A | N/A | Q7130A1006 | 160 | N/A | 24 | 35 | 160 | 60 | N/A | 2 | YES | 4-7 Vdc | NDR | N/A | TRUE
[24 empty] | 358 | M7164G1030 | N/A | N/A | N/A | N/A | 90 | N/A | 120 | 35 | 90 | 30 | N/A | 2 | N/A | 10.5-13.5 Vdc | N/A | N/A | TRUE
[24 empty] | 359 | M7183G1003 | M9185D1004 | N/A | N/A | Q7130A1006 | 160 | N/A | 24 | 60 | 160 | 60 | N/A | 1 | N/A | 4-7 Vdc | NDR | Use auxiliary shaft | TRUE
[24 empty] | 360 | M7184A1005 | M9184D1021 | N/A | N/A | Q7130A1006 | 160 | N/A | 24 | 150 | 160 | 60 | N/A | 2 | YES | 4-7 Vdc | NDR | N/A | TRUE
[24 empty] | 361 | M7184A1013 | N/A | N/A | N/A | N/A | N/A | N/A | 120 | 150 | 90 | 30 | N/A | 2 | N/A | 0.8-3.3 Vdc | NDR | N/A | TRUE
[24 empty] | 362 | M7184A1021 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 150 | 90 | 30 | N/A | 2 | N/A | 0.8-3.3 Vdc | NDR | N/A | TRUE
[24 empty] | 363 | M7185A1004 | M9185D1004 | N/A | N/A | Q7130A1006 | 160 | N/A | 24 | 60 | 160 | 60 | N/A | 2 | N/A | 4-7 Vdc | NDR | N/A | TRUE
[24 empty] | 364 | M7186G1000 | M9185D1004 | N/A | N/A | Q7130A1006 | 160 | N/A | 24 | 60 | 160 | 60 | N/A | 2 | YES | 4-7 Vdc | NDR | Use auxiliary shaft | TRUE
[24 empty] | 365 | M7261A1001 | N/A | N/A | N/A | N/A | 160 | N/A | 120 | 35 | 160 | 60 | N/A | 1 | N/A | 2-10 Vdc | NDR | Trane | TRUE
[24 empty] | 366 | M7272A1008 | M9185D1004 | 50017460-003 | N/A | Q7230A1005 | 90 | N/A | 120 | 25 | 90 | 30 | N/A | 2 | N/A | 2-10 Vdc | NDR | Trane | TRUE
[24 empty] | 367 | M7274A1006 | M9184D1021 | N/A | N/A | Q7230A1005 | 160 | N/A | 24 | 75 | 160 | 60 | N/A | 2 | N/A | 2-10 Vdc | M9184D1021 + Q7230A1005 | N/A | TRUE
[24 empty] | 368 | M7274G1003 | M9174D1007 | N/A | N/A | Q7230A1005 | 160 | N/A | 24 | 75 | 160 | 60 | N/A | 2 | N/A | 2-10 Vdc | M9184D1021 + Q7230A1005 | N/A | TRUE
[24 empty] | 369 | M7281A1007 | M7284A1004 | N/A | N/A | N/A | 90 | N/A | 120 | 150 | 90 | 30 | N/A | 1 | N/A | 4-20 mA | M7284A1004 | Includes 220741A | TRUE
[24 empty] | 370 | M7281C1003 | M9184D1021 | 50017460-003 | 220736B | Q7230A1005 | 90 | N/A | 120 | 150 | 90 | 30 | 2 | 1 | N/A | 4-20 mA | M7284C1000 | Includes 220741A | TRUE
[24 empty] | 371 | M7281C1011 | M9184D1021 | 50017460-003 | 220736B | Q7230A1005 | 160 | N/A | 120 | 150 | 160 | 60 | 2 | 1 | N/A | 4-20 mA | M7284C1018 | Includes 220741A | TRUE
[24 empty] | 372 | M7281Q1002 | M7284Q1009 | N/A | N/A | N/A | 90 | N/A | 120 | 150 | 90 | 30 | 2 | 1 | N/A | 4-20 mA | M7284Q1009 | Includes 203709D board | TRUE
[24 empty] | 373 | M7282A1006 | M9185D1004 | 50017460-003 | N/A | Q7230A1005 | 90 | N/A | 120 | 60 | 90 | 30 | N/A | 1 | N/A | 4-20 mA | M7285A1003 | Includes 220741A | TRUE
[24 empty] | 374 | M7282A1014 | N/A | N/A | N/A | N/A | 90 | N/A | 120 | 60 | 90 | 30 | N/A | 1 | N/A | 2-10 Vdc | NDR | Trane | TRUE
[24 empty] | 375 | M7282A1022 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 60 | 90 | 30 | N/A | 1 | N/A | 2-10 Vdc | NDR | Trane, with wiring harness | TRUE
[24 empty] | 376 | M7282B1004 | M9185D1004 | 50017460-003 | 220736A | Q7230A1005 | 90 | 25 | 120 | 60 | 90 | 30 | 1 | 1 | N/A | 2-10 Vdc | NDR | Trane | TRUE
[24 empty] | 377 | M7282B1012 | N/A | N/A | N/A | N/A | 90 | 25 | 24 | 60 | 90 | 30 | 1 | 1 | N/A | 2-10 Vdc | NDR | Trane | TRUE
[24 empty] | 378 | M7282C1002 | M9185D1004 | 50017460-003 | 220736B | Q7230A1005 | 90 | 35 & 80 | 120 | 60 | 90 | 30 | 2 | 1 | N/A | 2-10Vdc | NDR | Trane | TRUE
[24 empty] | 379 | M7282D1000 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 60 | 90/160 | 15/60 | N/A | 1 | N/A | 4-20 mA | NDR | Carrier, with 205118A | TRUE
[24 empty] | 380 | M7282D1018 | M7282D1000 | 50017460-001 | N/A | N/A | N/A | N/A | 24 | 60 | 90/160 | 15/60 | N/A | 1 | N/A | 4-20 mA | NDR | Carrier, with 205118A | TRUE
[24 empty] | 381 | M7282F1005 | M7282D1000 | N/A | 220736B | N/A | N/A | 13 & 35 | 24 | 60 | 90/160 | 15/60 | 2 | 1 | N/A | 4-20 mA | NDR | Carrier, 205118A and crank arm | TRUE
[24 empty] | 382 | M7284A1004 | N/A | N/A | N/A | N/A | 90 | N/A | 120 | 150 | 90 | 30 | N/A | 2 | N/A | 4-20 mA | N/A | Includes 220741A | TRUE
[24 empty] | 383 | M7284A1012 | N/A | N/A | N/A | N/A | 160 | N/A | 120 | 150 | 160 | 60 | N/A | 2 | N/A | 4-20 mA | N/A | Includes 220741A | TRUE
[24 empty] | 384 | M7284A1020 | M9184D1021 | 50017460-003 | N/A | Q7230A1005 | 160 | N/A | 120 | 150 | 160 | 60 | N/A | 2 | N/A | 4-20 mA | M7284A1012 | Includes 220741A | TRUE
[24 empty] | 385 | M7284A1038 | N/A | N/A | N/A | N/A | 90 | N/A | 120 | 75 | 90 | 15 | N/A | 2 | N/A | 4-20 mA | N/A | Includes 220741A | TRUE
[24 empty] | 386 | M7284A1046 | M7284A1004 | N/A | N/A | N/A | 90 | N/A | 120 | 150 | 90 | 30 | N/A | 2 | N/A | 4-20 mA | M7284A1004 | Includes 220741A | TRUE
[24 empty] | 387 | M7284A1053 | N/A | N/A | N/A | N/A | 90 | N/A | 120 | 150 | 90 | 30 | N/A | 2 | N/A | 2-10 Vdc | NDR | Trane | TRUE
[24 empty] | 388 | M7284A1061 | M9184D1021 | 50017460-003 | N/A | Q7230A1005 | 160 | N/A | 120 | 150 | 160 | 60 | N/A | 2 | N/A | 2-10 Vdc | NDR | Trane | TRUE
[24 empty] | 389 | M7284A1079 | N/A | N/A | N/A | N/A | 160 | N/A | 24 | 150 | 160 | 60 | N/A | 2 | N/A | 2-10 Vdc | N/A | N/A | TRUE
[24 empty] | 390 | M7284A1087 | N/A | N/A | N/A | N/A | 90 | N/A | 24 | 150 | 90 | 30 | N/A | 2 | N/A | 2-10 Vdc | NDR | Trane | TRUE
[24 empty] | 391 | M7284C1000 | N/A | N/A | N/A | N/A | 90 | N/A | 120 | 150 | 90 | 30 | 2 | 2 | N/A | 4-20 mA | N/A | Includes 220741A | TRUE
[24 empty] | 392 | M7284C1018 | M7284C1000 | N/A | N/A | N/A | 160 | N/A | 120 | 150 | 160 | 60 | 2 | 2 | N/A | 4-20 mA | M7284C1000 | Includes 220741A | TRUE
[24 empty] | 393 | M7284C1026 | M9184D1021 | 50017460-003 | 220736B | Q7230A1005 | 90 | N/A | 120 | 150 | 90 | 30 | 2 | 2 | N/A | 4-20 mA | M7284C1000 | Includes 220741A | TRUE
[24 empty] | 394 | M7284C1034 | M9184D1021 | 50017460-003 | 220736B | Q7230A1005 | 160 | N/A | 120 | 150 | 160 | 60 | 2 | 2 | N/A | 4-20 mA | M7284C1018 | Includes 220741A | TRUE
[24 empty] | 395 | M7284C1042 | M9184D1021 | N/A | 220736B | Q7230A1005 | N/A | N/A | 100/200 | 150 | 90 | 30 | 2 | 2 | N/A | 4-20 mA | NDR | International, includes 220741A | TRUE
[24 empty] | 396 | M7284C1059 | M7284C1083 | N/A | N/A | 220738A | N/A | N/A | 24 | 150 | 90 | 30 | 2 | 2 | YES | 4-20 mA | M7284C1083 | Enhanced | TRUE
[24 empty] | 397 | M7284C1067 | M7284C1091 | N/A | N/A | 220738A | N/A | N/A | 24 | 150 | 160 | 60 | 2 | 2 | YES | 4-20 mA | M7284C1091 | Enhanced | TRUE
[24 empty] | 398 | M7284G1001 | M9184D1021 | N/A | N/A | Q7230A1005 | 160 | N/A | 24 | 150 | 160 | 60 | N/A | 2 | N/A | 2-10 Vdc | M7284A1079 | N/A | TRUE
[24 empty] | 399 | M7284Q1009 | N/A | N/A | N/A | N/A | 90 | N/A | 120 | 150 | 90 | 30 | 2 | 2 | N/A | 4-20 mA | N/A | Includes 203709D board | TRUE
[24 empty] | 400 | M7284Q1017 | M7284Q1009 | N/A | N/A | N/A | 160 | N/A | 120 | 150 | 160 | 60 | 2 | 2 | YES | 4-20 mA | M7284Q1009 | Includes 203709D board | TRUE
[24 empty] | 401 | M7284Q1025 | M7284Q1009 | N/A | N/A | N/A | N/A | N/A | 100/200 | 150 | 90 | 30 | N/A | N/A | N/A | 4-20 mA | NDR | International, includes 203709D | TRUE
[24 empty] | 402 | M7284Q1033 | M7284Q1082 | N/A | N/A | 220738A | N/A | N/A | 24 | 150 | 90 | 30 | 2 | 2 | YES | 4-20 mA | M7284Q1082 | Enhanced | TRUE
[24 empty] | 403 | M7284Q1041 | M7284Q1090 | N/A | N/A | 220738A | N/A | N/A | 24 | 150 | 160 | 60 | 2 | 2 | YES | 4-20 mA | M7284Q1090 | Enhanced | TRUE
[24 empty] | 404 | M7285A1003 | N/A | N/A | N/A | N/A | 90 | N/A | 120 | 60 | 90 | 30 | N/A | 2 | N/A | 4-20 mA | N/A | Includes 220741A | TRUE
[24 empty] | 405 | M7285A1011 | M7285A1003 | N/A | N/A | N/A | 160 | N/A | 120 | 60 | 160 | 60 | N/A | 2 | N/A | 4-20 mA | M7285A1003 | Includes 220741A | TRUE
[24 empty] | 406 | M7285A1029 | M9185D1004 | N/A | N/A | Q7230A1005 | 160 | N/A | 24 | 60 | 160 | 60 | N/A | 2 | N/A | 2-10 Vdc | NDR | UL555S | TRUE
[24 empty] | 407 | M7285A1037 | M9185D1004 | N/A | N/A | Q7230A1005 | 160 | N/A | 24 | 60 | 160 | 60 | N/A | 2 | N/A | 2-10 Vdc | NDR | UL555S | TRUE
[24 empty] | 408 | M7285A1045 | N/A | N/A | N/A | N/A | 160 | N/A | 24 | 60 | 160 | 60 | N/A | 2 | N/A | 2-10 Vdc | N/A | N/A | TRUE
[24 empty] | 409 | M7285A1052 | M9185D1004 | N/A | N/A | Q7230A1005 | 90 | N/A | 24 | 60 | 90 | 30 | N/A | 2 | N/A | 2-10 Vdc | NDR | N/A | TRUE
[24 empty] | 410 | M7285B1001 | M9185D1004 | N/A | 220736A | Q7230A1005 | 90 | 25 | 24 | 60 | 90 | 30 | 1 | 2 | N/A | 2-10 Vdc | NDR | Trane | TRUE
[24 empty] | 411 | M7285C1009 | N/A | N/A | N/A | N/A | 90 | N/A | 120 | 60 | 90 | 30 | 2 | 2 | N/A | 4-20 mA | N/A | Includes 220741A | TRUE
[24 empty] | 412 | M7285C1017 | M7285C1009 | N/A | N/A | N/A | 160 | N/A | 120 | 60 | 160 | 60 | 2 | 2 | N/A | 4-20 mA | M7285C1009 | Includes 220741A | TRUE
[24 empty] | 413 | M7285C1025 | M9185D1004 | N/A | 220736B | Q7230A1005 | 160 | N/A | 24 | 60 | 160 | 60 | 2 | 2 | N/A | 2-10 Vdc | NDR | N/A | TRUE
[24 empty] | 414 | M7285C1033 | M9185D1004 | N/A | 220736B | Q7230A1005 | 160 | N/A | 24 | 60 | 160 | 60 | 2 | 2 | N/A | 2-10 Vdc | NDR | N/A | TRUE
[24 empty] | 415 | M7285Q1008 | N/A | N/A | N/A | N/A | 90 | N/A | 120 | 60 | 90 | 30 | 2 | 2 | N/A | 4-20 mA | N/A | Includes 203709D board | TRUE
[24 empty] | 416 | M7286G1009 | N/A | N/A | N/A | N/A | 160 | N/A | 24 | 60 | 160 | 60 | N/A | 2 | N/A | 2-10 Vdc | N/A | N/A | TRUE
[24 empty] | 417 | M7294A1002 | M9194D1003 | 50017460-003 | N/A | Q7230A1005 | 90 | N/A | 120 | 300 | 90 | 60 | N/A | 2 | N/A | 4-20 mA | M7294Q1007 | Includes 220741A | TRUE
[24 empty] | 418 | M7294A1010 | N/A | N/A | N/A | N/A | 160 | N/A | 24 | 300 | 160 | 120 | N/A | 2 | N/A | 2-10 Vdc | N/A | N/A | TRUE
[24 empty] | 419 | M7294G1009 | M7294A1010 | N/A | N/A | N/A | 160 | N/A | 24 | 300 | 160 | 120 | N/A | 2 | N/A | 2-10 Vdc | M7294A1010 | N/A | TRUE
[24 empty] | 420 | M7294Q1007 | N/A | N/A | N/A | N/A | 90 | N/A | 120 | 300 | 90 | 60 | 2 | 2 | N/A | 4-20 mA | N/A | Includes 203709D board | TRUE
[24 empty] | 421 | M734A1007 | N/A | N/A | N/A | N/A | N/A | N/A | 120 | 35 | 90 | 30 | N/A | N/A | N/A | W936 | M7964A1001 | Special circuit | TRUE
[24 empty] | 422 | M734A1015 | N/A | N/A | N/A | N/A | N/A | N/A | 120 | 35 | 90 | 30 | N/A | N/A | N/A | W936 | M7964A1001 | Special circuit | FALSE
[24 empty] | 423 | M734A1023 | N/A | N/A | N/A | N/A | N/A | N/A | 120 | 35 | 90 | 30 | N/A | N/A | N/A | W936 | M7964A1001 | Special circuit | FALSE
[24 empty] | 424 | M734B1006 | N/A | N/A | N/A | N/A | N/A | N/A | 120 | 35 | 90 | 28 | N/A | N/A | N/A | W936 | NDR | Special circuit | FALSE
[24 empty] | 425 | M734B1014 | N/A | N/A | N/A | N/A | N/A | N/A | 240 | 35 | 90 | 28 | N/A | N/A | N/A | W936 | NDR | Special circuit | FALSE
[24 empty] | 426 | M734B1022 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 35 | 90 | 28 | N/A | N/A | N/A | W936 | NDR | Special circuit | FALSE
[24 empty] | 427 | M734B1030 | N/A | N/A | N/A | N/A | N/A | N/A | 240 | 35 | 160 | 50 | N/A | N/A | N/A | W936 | NDR | Special circuit | FALSE
[24 empty] | 428 | M734B1048 | N/A | N/A | N/A | N/A | N/A | N/A | 120 | 35 | 160 | 50 | N/A | N/A | N/A | W936 | NDR | Special circuit | FALSE
[24 empty] | 429 | M734C1005 | N/A | N/A | N/A | N/A | N/A | N/A | 120 | 35 | 90 | 28 | N/A | N/A | N/A | W936 | NDR | Special circuit | FALSE
[24 empty] | 430 | M734C1013 | N/A | N/A | N/A | N/A | N/A | N/A | 120 | 35 | 90 | 28 | N/A | N/A | N/A | W936 | NDR | Special circuit | FALSE
[24 empty] | 431 | M734C1021 | N/A | N/A | N/A | N/A | N/A | N/A | 120 | 35 | 90 | 28 | N/A | N/A | N/A | W936 | NDR | Special circuit | FALSE
[24 empty] | 432 | M734D1004 | M9164D1009 | 50017460-003 | N/A | Q7330A1004 | 160° | N/A | 120 | 35 | 160 | 50 | N/A | N/A | N/A | W936 | NDR | N/A | FALSE
[24 empty] | 433 | M734D1012 | M9164D1009 | 50017460-003 | N/A | Q7330A1004 | 90° | N/A | 120 | 35 | 90 | 28 | N/A | N/A | N/A | W936 | NDR | N/A | FALSE
[24 empty] | 434 | M734D1020 | M9164D1009 | 50017460-001 | N/A | Q7330A1004 | 160° | N/A | 240 | 35 | 160 | 50 | N/A | N/A | N/A | W936 | NDR | N/A | FALSE
[24 empty] | 435 | M734D1038 | M9164D1009 | N/A | N/A | Q7330A1004 | 160° | N/A | 24 | 35 | 160 | 50 | N/A | N/A | N/A | W936 | NDR | N/A | FALSE
[24 empty] | 436 | M734D1046 | M9164D1009 | N/A | 220736A | Q7330A1004 | 90° | N/A | 24 | 35 | 90 | 28 | 1 | N/A | N/A | W936 | NDR | N/A | FALSE
[24 empty] | 437 | M734D1053 | M9164D1009 | N/A | 220736A | Q7330A1004 | 160° | N/A | 24 | 35 | 160 | 50 | 1 | N/A | N/A | W936 | NDR | N/A | FALSE
[24 empty] | 438 | M734E ALL | M9164D1009 | N/A | N/A | Q7330A1004 | N/A | N/A | N/A | 35 | N/A | N/A | N/A | N/A | N/A | W936 | NDR | Use aux end of N.C. motor | FALSE
[24 empty] | 439 | M734F ALL | M9164D1009 | N/A | N/A | Q7330A1004 | N/A | N/A | N/A | 75 | N/A | N/A | N/A | N/A | N/A | W936 | NDR | N/A | FALSE
[24 empty] | 440 | M734G ALL | M9164D1009 | N/A | N/A | Q7330A1004 | N/A | N/A | N/A | 75 | N/A | N/A | N/A | N/A | N/A | W936 | NDR | N/A | FALSE
[24 empty] | 441 | M734H1000 | M9164D1009 | 50017460-003 | N/A | Q7130A1006 | 90° | N/A | 120 | 35 | 90 | 28 | N/A | N/A | N/A | 10.5-13.5 Vdc | M7164G1030 | Adjust for 10.5-13.5 Vdc, select CCW rotation | FALSE
[24 empty] | 442 | M734H1018 | M9164D1009 | 50017460-003 | N/A | Q7130A1006 | 90° | N/A | 120 | 35 | 90 | 28 | N/A | N/A | N/A | 4 - 7 Vdc | NDR | Adjust for 4-7 Vdc, Select CCW | FALSE
[24 empty] | 443 | M734H1026 | M9164D1009 | N/A | N/A | Q7130A1006 | 160° | N/A | 24 | 35 | 160 | 50 | N/A | N/A | N/A | 4 - 7 Vdc | NDR | Adjust for 4-7 Vdc, Select CCW | FALSE
[24 empty] | 444 | M734H1034 | M9164D1009 | N/A | N/A | Q7130A1006 | 90° | N/A | 24 | 35 | 90 | 30 | N/A | N/A | N/A | 10.5-13.5 Vdc | M7164G1030 | Adjust for 10.5-13.5 Vdc, select CCW rotation | FALSE
[24 empty] | 445 | M734J1007 | M9164D1009 | 50017460-003 | N/A | Q7130A1006 | 160° | N/A | 120 | 35 | 160 | 50 | N/A | N/A | N/A | 6 - 9 Vdc | NDR | Adjsut for 6-9 Vdc | FALSE
[24 empty] | 446 | M734J1015 | M9164D1009 | N/A | N/A | Q7130A1006 | 160° | N/A | 24 | 35 | 160 | 50 | N/A | N/A | N/A | 4 - 7 Vdc | NDR | Adjust for 4-7 Vdc | FALSE
[24 empty] | 447 | M734J1023 | M9164D1009 | N/A | N/A | Q7130A1006 | 90° | N/A | 24 | 35 | 90 | 30 | N/A | N/A | N/A | 10.5-13.5 Vdc | M7164A1017 | Adjust for 10.5-13.5 Vdc | FALSE
[24 empty] | 448 | M734J1031 | M9164D1009 | 50017460-003 | N/A | Q7130A1006 | 90° | N/A | 120 | 35 | 90 | 30 | N/A | N/A | N/A | 10.5-13.5 Vdc | NDR | Adjust for 10.5-13.5 Vdc | FALSE
[24 empty] | 449 | M734J1049 | M9164D1009 | N/A | N/A | Q7130A1006 | 160° | N/A | 24 | 35 | 160 | 50 | N/A | N/A | N/A | 10.5-13.5 Vdc | NDR | Adjust for 10.5-13.5 Vdc | FALSE
[24 empty] | 450 | M734J1056 | M9164D1009 | N/A | N/A | Q7130A1006 | 90° | N/A | 24 | 35 | 90 | 30 | N/A | N/A | N/A | 10.5-13.5 Vdc | M7164A1017 | Adjust for 10.5-13.5 Vdc | FALSE
[24 empty] | 451 | M734J1064 | M9164D1009 | 50017460-003 | N/A | Q7130A1006 | 90° | N/A | 120 | 35 | 90 | 30 | N/A | N/A | N/A | 6 - 9 Vdc | NDR | Adjsut for 6-9 Vdc | FALSE
[24 empty] | 452 | M734J1072 | M9164D1009 | 50017460-003 | 220736A | Q7130A1006 | 160° | N/A | 120 | 35 | 160 | 50 | 1 | N/A | N/A | 4 - 7 Vdc | NDR | Adjust for 4-7 Vdc | FALSE
[24 empty] | 453 | M734K1006 | N/A | N/A | N/A | N/A | N/A | N/A | 120 | 35 | 160 | 50 | N/A | N/A | N/A | 4 - 7 Vdc, 3 w, 11 Vdc out | NDR | 3 wire output | FALSE
[24 empty] | 454 | M734K1014 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 35 | 160 | 50 | N/A | N/A | N/A | 4 - 7 Vdc, 3 w, 11 Vdc out | NDR | 3 wire output | FALSE
[24 empty] | 455 | M7361A1000 | M9164D1009 | 50017460-003 | N/A | Q7330A1004 | 90 | N/A | 120 | 35 | 90 | 30 | N/A | 1 | N/A | W936 | NDR | N/A | FALSE
[24 empty] | 456 | M7361A1018 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 35 | 160 | 60 | N/A | 1 | N/A | W936 | NDR | Liebert, with 203709B board | TRUE
[24 empty] | 457 | M7364A1007 | M9164D1009 | 50017460-003 | N/A | Q7330A1004 | 160 | N/A | 120 | 35 | 160 | 60 | N/A | 2 | YES | W936 | NDR | N/A | TRUE
[24 empty] | 458 | M7364A1015 | M9164D1009 | 50017460-003 | N/A | Q7330A1004 | 90 | N/A | 120 | 35 | 90 | 30 | N/A | 2 | YES | W936 | NDR | N/A | TRUE
[24 empty] | 459 | M7364A1023 | M9164D1009 | N/A | N/A | Q7330A1004 | 160 | N/A | 24 | 35 | 160 | 60 | N/A | 2 | YES | W936 | NDR | N/A | TRUE
[24 empty] | 460 | M7364A1031 | M9164A1070 | 50017460-001 | N/A | Q7330A1004 | N/A | N/A | 24 | 35 | 160 | 60 | N/A | 2 | N/A | W936 | NDR | Liebert | TRUE
[24 empty] | 461 | M7381A1006 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 150 | 160 | 60 | N/A | 1 | N/A | W936 | NDR | Liebert, with 203709B board | TRUE
[24 empty] | 462 | M7382A1005 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 60 | 160 | 60 | N/A | 1 | N/A | W936 | NDR | Liebert | TRUE
[24 empty] | 463 | M7384A1003 | M9184D1021 | N/A | N/A | Q7330A1004 | 160 | N/A | 24 | 150 | 160 | 60 | N/A | 2 | YES | W936 | NDR | N/A | TRUE
[24 empty] | 464 | M7384A1011 | M9184D1021 | N/A | N/A | Q7330A1004 | 90 | N/A | 24 | 150 | 90 | 30 | N/A | 2 | N/A | W936 | NDR | N/A | TRUE
[24 empty] | 465 | M7384A1029 | NDR | N/A | N/A | N/A | N/A | N/A | 24 | 150 | 160 | 60 | N/A | 2 | N/A | W936 | NDR | Liebert | TRUE
[24 empty] | 466 | M7385A1002 | M9185D1004 | N/A | N/A | Q7330A1004 | 90 | N/A | 24 | 60 | 90 | 30 | N/A | 2 | YES | W936 | NDR | N/A | TRUE
[24 empty] | 467 | M7385A1010 | M9185D1004 | 50017460-001 | N/A | Q7330A1004 | 160 | N/A | 24 | 60 | 160 | 60 | N/A | 2 | YES | W936 | NDR | Includes isolation transformer | TRUE
[24 empty] | 468 | M7385A1028 | M9185D1004 | 50017460-003 | N/A | Q7330A1004 | 160 | N/A | 120 | 60 | 160 | 60 | N/A | 2 | N/A | W936 | NDR | N/A | TRUE
[24 empty] | 469 | M7385A1036 | M9185D1004 | N/A | N/A | Q7330A1004 | 160 | N/A | 24 | 60 | 160 | 60 | N/A | 2 | YES | W936 | NDR | N/A | TRUE
[24 empty] | 470 | M7385A1044 | M9185A1018 | 50017460-001 | N/A | Q7330A1004 | N/A | N/A | 24 | 60 | 160 | 60 | N/A | 2 | N/A | W936 | NDR | Liebert | TRUE
[24 empty] | 471 | M7405A1008 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 25 | 90° | 90 | N/A | N/A | N/A | Digital | NDR | N/A | TRUE
[24 empty] | 472 | M7405A1016 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 25 | 90° | 90 | N/A | N/A | N/A | Digital | NDR | N/A | FALSE
[24 empty] | 473 | M7405A1018 | N/A | N/A | N/A | N/A | N/A | N/A | 24 Vac | 25 lb-in | 90 degrees | 90 seconds (60 Hz) | N/A | N/A | N/A | Modulating | N/A | N/A | TRUE
[24 empty] | 474 | M7410E1010 | M7410F1000 | N/A | N/A | N/A | N/A | N/A | 24 Vac | 40.5 lb | 0.25 inch | 150 s at 50 Hz, 125 s at 60 Hz | N/A | N/A | N/A | 0 to 10 Vdc, 2 to 10 Vdc | N/A | N/A | TRUE
[24 empty] | 475 | M7410E1036 | M7410F1000 | N/A | N/A | N/A | N/A | N/A | 24 Vac | 40.5 lb | 0.25 inch | 150 s at 50 Hz, 125 s at 60 Hz | N/A | N/A | N/A | 0 to 10 Vdc, 2 to 10 Vdc | N/A | N/A | TRUE
[24 empty] | 476 | M7410F1000 | N/A | N/A | N/A | N/A | N/A | N/A | 24 Vac | 40.5 lb | 0.25 inch | 150 s at 50 Hz, 125 s at 60 Hz | N/A | N/A | N/A | 0 to 10 Vdc, 2 to 10 Vdc | N/A | N/A | TRUE
[24 empty] | 477 | M7415A1006 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 25 | 90° | 90 | N/A | N/A | N/A | Thermistor | M7415A1006 | N/A | TRUE
[24 empty] | 478 | M7415A1014 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 25 | 90° | 90 | N/A | N/A | N/A | Thermistor | M7415A1014 | N/A | TRUE
[24 empty] | 479 | M7415A1022 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 25 | 90° | 90 | N/A | N/A | N/A | Thermistor | M7415A1006 | N/A | FALSE
[24 empty] | 480 | M7415A1048 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 25 | 90° | 90 | N/A | N/A | N/A | Thermistor | M7415A1048 | N/A | FALSE
[24 empty] | 481 | M7415B1004 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 25 | 90° | 90 | N/A | N/A | N/A | Thermistor | M7415B1004 | N/A | FALSE
[24 empty] | 482 | M741B1001 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 150 | 90 | 30 | N/A | N/A | N/A | BRCS | NDR | Cleaver Brooks BRCS | TRUE
[24 empty] | 483 | M741B1019 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 150 | 90 | 30 | N/A | N/A | N/A | BRCS | NDR | BRCS | FALSE
[24 empty] | 484 | M744A1006 | M9184D1021 | N/A | N/A | Q7330A1004 | 160° | N/A | 24 | 150 | 160 | 60 | N/A | N/A | N/A | W936 | NDR | N/A | FALSE
[24 empty] | 485 | M744A1014 | M9184D1021 | N/A | N/A | Q7330A1004 | 90° | N/A | 24 | 150 | 90 | 30 | N/A | N/A | N/A | W936 | NDR | N/A | FALSE
[24 empty] | 486 | M744A1022 | M9184D1021 | 50017460-003 | N/A | Q7330A1004 | 90° | N/A | 120 | 150 | 90 | 30 | N/A | N/A | N/A | W936 | NDR | N/A | FALSE
[24 empty] | 487 | M744B ALL | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 150 | N/A | N/A | N/A | N/A | N/A | W936 | NDR | N/A | FALSE
[24 empty] | 488 | M744D1003 | M9184D1021 | N/A | N/A | Q7130A1006 | 160° | N/A | 24 | 150 | 160 | 60 | N/A | N/A | N/A | 4 - 7 Vdc | NDR | Adjust for 4-7 Vdc | FALSE
[24 empty] | 489 | M744D1011 | M9184D1021 | N/A | N/A | Q7130A1006 | 160° | N/A | 24 | 150 | 160 | 60 | N/A | N/A | N/A | 4 - 7 Vdc | NDR | Adjust for 4-7 Vdc | FALSE
[24 empty] | 490 | M744D1029 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 150 | 90 | 30 | N/A | N/A | N/A | 0.8 - 3.3 Vdc | NDR | N/A | FALSE
[24 empty] | 491 | M744D1037 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 150 | 90 | 120 | N/A | N/A | N/A | 0.8 - 3.3 Vdc | NDR | N/A | FALSE
[24 empty] | 492 | M744D1045 | N/A | N/A | N/A | N/A | N/A | N/A | 120 | 150 | 90 | 30 | N/A | N/A | N/A | 0.8 - 3.3 Vdc | NDR | N/A | FALSE
[24 empty] | 493 | M744E1002 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 50 | 160 | 60 | N/A | N/A | N/A | 2 - 10 Vdc | NDR | Micronik | FALSE
[24 empty] | 494 | M744F1001 | M9184D1021 | N/A | N/A | Q7330A1004 | 160° | N/A | 24 | 150 | 160 | 60 | N/A | N/A | N/A | W936 | NDR | N/A | FALSE
[24 empty] | 495 | M744G1000 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 150 | 160 | 60 | N/A | N/A | N/A | 4 - 7 Vdc, 3 w, 11 Vdc out | NDR | 3 wire output | FALSE
[24 empty] | 496 | M744J1006 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 150 | 90 | 30 | N/A | N/A | N/A | 0 - 2.5 Vdc | NDR | N/A | FALSE
[24 empty] | 497 | M744S1005 | M9184D1021 | 50017460-003 | N/A | Q7230A1005 | 90° | N/A | 120 | 150 | 90 | 30 | N/A | N/A | N/A | 4 - 20 mA | M7284A1004 | Adjust for 4-20 mA | FALSE
[24 empty] | 498 | M744S1013 | M9184D1021 | 50017460-003 | N/A | Q7230A1005 | 160° | N/A | 120 | 150 | 160 | 60 | N/A | N/A | N/A | 4 - 20 mA | M7284A1012 | Adjust for 4-20 mA | FALSE
[24 empty] | 499 | M744T1004 | M9184D1021 | 50017460-003 | 220736B | Q7230A1005 | 90° | N/A | 120 | 150 | 90 | 30 | 2 | N/A | N/A | 4 - 20 mA | M7284C1000 | Adjust for 4-20 mA | FALSE
[24 empty] | 500 | M744T1012 | M9184D1021 | 50017460-003 | 220736B | Q7230A1005 | 160° | N/A | 120 | 150 | 160 | 60 | 2 | N/A | N/A | 4 - 20 mA | M7284C1018 | Adjust for 4-20 mA | FALSE
[24 empty] | 501 | M744Y1009 | M9184D1021 | 50017460-003 | 220736B | Q7230A1005 | 90° | N/A | 120 | 150 | 90 | 30 | 2 | N/A | N/A | 4 - 20 mA | M7284Q1009 | Adjust for desired range | FALSE
[24 empty] | 502 | M744Y1017 | M9184D1021 | 50017460-003 | 220736B | Q7230A1005 | 160° | N/A | 120 | 150 | 160 | 60 | 2 | N/A | N/A | 4 - 20 mA | M7284Q1009 | Adjust for desired range | FALSE
[24 empty] | 503 | M745A1003 | M9185D1004 | N/A | N/A | Q7330A1004 | 90° | N/A | 24 | 50 | 90 | 30 | N/A | N/A | N/A | W936 | NDR | N/A | FALSE
[24 empty] | 504 | M745A1011 | M9185D1004 | N/A | N/A | Q7330A1004 | 160° | N/A | 24 | 50 | 160 | 60 | N/A | N/A | N/A | W936 | NDR | N/A | FALSE
[24 empty] | 505 | M745A1029 | M9185D1004 | 50017460-003 | N/A | Q7330A1004 | 160° | N/A | 120 | 50 | 160 | 60 | N/A | N/A | N/A | W936 | NDR | N/A | FALSE
[24 empty] | 506 | M745B1002 | M9185D1004 | N/A | N/A | Q7330A1004 | 160° | N/A | 24 | 50 | 160 | 60 | N/A | N/A | N/A | W936 | NDR | Use aux end of N.C. motor | FALSE
[24 empty] | 507 | M745C1001 | M9185D1004 | N/A | N/A | Q7330A1004 | 160° | N/A | 24 | 50 | 160 | 60 | N/A | N/A | N/A | W936 | NDR | Used with W936 & W945 systems | FALSE
[24 empty] | 508 | M745D ALL | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 50 | 160 | 60 | N/A | N/A | N/A | N/A | NDR | N/A | FALSE
[24 empty] | 509 | M745E1009 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 50 | 160 | 60 | N/A | N/A | N/A | W936 | NDR | N/A | FALSE
[24 empty] | 510 | M745F1008 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 50 | 160 | 60 | N/A | N/A | N/A | N/A | NDR | N/A | FALSE
[24 empty] | 511 | M745G1007 | M9185D1004 | N/A | N/A | Q7130A1006 | 160° | N/A | 24 | 50 | 160 | 60 | N/A | N/A | N/A | 4 - 7 Vdc | NDR | Adjust for 4-7 Vdc, Select CCW | FALSE
[24 empty] | 512 | M745H1006 | M9185D1004 | N/A | N/A | Q7630A1001 | 160° | N/A | 24 | 50 | 160 | 60 | N/A | N/A | N/A | 14 - 17 Vdc | NDR | N/A | FALSE
[24 empty] | 513 | M745J1003 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 50 | 160 | 60 | N/A | N/A | N/A | 4 - 7 Vdc, 3 w, 11 Vdc out | NDR | 3 wire output | FALSE
[24 empty] | 514 | M745K1002 | M9185D1004 | N/A | N/A | Q7630A1001 | 90° | N/A | 24 | 50 | 90 | 35 | N/A | N/A | N/A | 14 - 17 Vdc | NDR | Lennox Special, select CCW rotation | FALSE
[24 empty] | 515 | M745L1001 | M9185D1004 | N/A | N/A | Q7630A1001 | 90° | N/A | 24 | 50 | 90 | 35 | N/A | N/A | N/A | 14 - 17 Vdc | NDR | Lennox Special | FALSE
[24 empty] | 516 | M745L1019 | M9185D1004 | 50017460-003 | N/A | Q7630A1001 | 160° | N/A | 120 | 50 | 160 | 60 | N/A | N/A | N/A | 14 - 17 Vdc | NDR | York Special | FALSE
[24 empty] | 517 | M745L1027 | M9185D1004 | N/A | N/A | Q7630A1001 | 160° | N/A | 24 | 50 | 160 | 60 | N/A | N/A | N/A | 14 - 17 Vdc | NDR | N/A | FALSE
[24 empty] | 518 | M745L1035 | M9185D1004 | N/A | N/A | Q7630A1001 | 90° | N/A | 24 | 50 | 90 | 35 | N/A | N/A | N/A | 14 - 17 Vdc | NDR | N/A | FALSE
[24 empty] | 519 | M745L1043 | M9185D1004 | N/A | N/A | Q7630A1001 | 90° | N/A | 24 | 50 | 90 | 35 | N/A | N/A | N/A | 14 - 17 Vdc | NDR | N/A | FALSE
[24 empty] | 520 | M745M1000 | M9185D1004 | N/A | N/A | Q7130A1006 | 160° | N/A | 24 | 50 | 160 | 60 | N/A | N/A | N/A | 6 - 9 Vdc | NDR | Adjust for 6-9 Vdc, use auiliary end | FALSE
[24 empty] | 521 | M745M1018 | M9185D1004 | N/A | N/A | Q7130A1006 | 90° | N/A | 24 | 50 | 90 | 35 | N/A | N/A | N/A | 10.5-13.5 Vdc | NDR | Adjust for 10.5-13.5 Vdc, use auiliary end | FALSE
[24 empty] | 522 | M745M1026 | M9185D1004 | N/A | N/A | Q7130A1006 | 160° | N/A | 24 | 50 | 160 | 60 | N/A | N/A | N/A | 4 - 7 Vdc | NDR | Adjust for 4-7 Vdc, use auiliary end | FALSE
[24 empty] | 523 | M745M1034 | M9185D1004 | N/A | N/A | Q7130A1006 | 160° | N/A | 24 | 50 | 160 | 60 | N/A | N/A | N/A | 4 - 7 Vdc | NDR | Adjust for 4-7 Vdc, use auiliary end | FALSE
[24 empty] | 524 | M745M1042 | M9185D1004 | N/A | N/A | Q7130A1006 | 160° | N/A | 24 | 50 | 160 | 60 | N/A | N/A | N/A | 4 - 7 Vdc | NDR | Adjust for 4-7 Vdc, use auiliary end | FALSE
[24 empty] | 525 | M745N1009 | M9185D1004 | N/A | N/A | Q7130A1006 | 90° | N/A | 24 | 50 | 90 | 35 | N/A | N/A | N/A | 10.5-13.5 Vdc | NDR | Adjust for 10.5-13.5 Vdc, select CCW rotation | FALSE
[24 empty] | 526 | M745N1017 | M9185D1004 | N/A | N/A | Q7130A1006 | 160° | N/A | 24 | 50 | 160 | 60 | N/A | N/A | N/A | 10.5-13.5 Vdc | NDR | Adjust for 10.5-13.5 Vdc, select CCW rotation | FALSE
[24 empty] | 527 | M745N1025 | M9185D1004 | N/A | N/A | Q7130A1006 | 160° | N/A | 24 | 50 | 160 | 60 | N/A | N/A | N/A | 6 - 9 Vdc | NDR | Adjust for 4-7 Vdc, Select CCW | FALSE
[24 empty] | 528 | M745P1007 | M9185D1004 | N/A | N/A | Q7130A1006 | 160° | N/A | 24 | 50 | 160 | 60 | N/A | N/A | N/A | 4 - 7 Vdc | NDR | Adjust for 4-7 Vdc | FALSE
[24 empty] | 529 | M745P1015 | M9185D1004 | N/A | N/A | Q7130A1006 | 90° | N/A | 24 | 50 | 90 | 35 | N/A | N/A | N/A | 10.5-13.5 Vdc | NDR | Adjust for 10.5-13.5 Vdc | FALSE
[24 empty] | 530 | M745Q1006 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 50 | 90 | 35 | N/A | N/A | N/A | N/A | NDR | N/A | FALSE
[24 empty] | 531 | M745S1002 | M9185D1004 | 50017460-003 | N/A | Q7230A1005 | 90° | N/A | 120 | 50 | 90 | 30 | N/A | N/A | N/A | 4 - 20 mA | M7285A1003 | Adjust for 4-20 mA | FALSE
[24 empty] | 532 | M745S1010 | M9185D1004 | 50017460-003 | N/A | Q7230A1005 | 160° | N/A | 120 | 50 | 160 | 60 | N/A | N/A | N/A | 4 - 20 mA | M7285A1003 | Adjust for 4-20 mA | FALSE
[24 empty] | 533 | M745T1001 | M9185D1004 | 50017460-003 | 220736B | Q7230A1005 | 90° | N/A | 120 | 50 | 90 | 30 | 2 | N/A | N/A | 4 - 20 mA | M7285C1009 | Adjust for 4-20 mA | FALSE
[24 empty] | 534 | M745T1019 | M9185D1004 | 50017460-003 | 220736B | Q7230A1005 | 160° | N/A | 120 | 50 | 160 | 60 | 2 | N/A | N/A | 4 - 20 mA | M7285C1009 | Adjust for 4-20 mA | FALSE
[24 empty] | 535 | M745Y1006 | M9185D1004 | 50017460-003 | 220736B | Q7230A1005 | 90° | N/A | 120 | 50 | 90 | 30 | 2 | N/A | N/A | 4 - 20 mA | M7285Q1008 | Adjust for desired range | FALSE
[24 empty] | 536 | M745Y1014 | M9185D1004 | 50017460-003 | 220736B | Q7230A1005 | 160° | N/A | 120 | 50 | 160 | 60 | 2 | N/A | N/A | 4 - 20 mA | M7285Q1008 | Adjust for desired range | FALSE
[24 empty] | 537 | M7484A1002 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 150 | 90 | 30 | N/A | 2 | N/A | BRCS | NDR | Cleaver Brooks | FALSE
[24 empty] | 538 | M7484A1010 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 150 | 90 | 30 | N/A | 2 | N/A | BRCS | NDR | N/A | TRUE
[24 empty] | 539 | M765A1001 | M9185D1004 | N/A | N/A | Q7630A1001 | 160° | N/A | 24 | 25 | 160 | 40 | N/A | N/A | N/A | W936 | NDR | N/A | TRUE
[24 empty] | 540 | M765A1019 | M9185D1004 | N/A | N/A | Q7330A1004 | 90° | N/A | 24 | 25 | 90 | 25 | N/A | N/A | N/A | W936 | NDR | N/A | FALSE
[24 empty] | 541 | M765K1000 | M9185D1004 | N/A | N/A | Q7630A1001 | 90° | N/A | 24 | 25 | 90 | 25 | N/A | N/A | N/A | 14 - 17 Vdc | NDR | Select CCW rotation | FALSE
[24 empty] | 542 | M765L1009 | M9185D1004 | N/A | N/A | Q7630A1001 | 160° | N/A | 24 | 25 | 160 | 40 | N/A | N/A | N/A | 14 - 17 Vdc | NDR | N/A | FALSE
[24 empty] | 543 | M765L1017 | M9185D1004 | N/A | N/A | Q7630A1001 | 90° | N/A | 24 | 25 | 90 | 25 | N/A | N/A | N/A | 14 - 17 Vdc | NDR | N/A | FALSE
[24 empty] | 544 | M765L1025 | M9185D1004 | 50017460-003 | N/A | Q7630A1001 | 90° | N/A | 120 | 25 | 90 | 25 | N/A | N/A | N/A | 14 - 17 Vdc | NDR | N/A | FALSE
[24 empty] | 545 | M765N1007 | M9185D1004 | N/A | N/A | Q7130A1006 | 90° | N/A | 24 | 25 | 90 | 25 | N/A | N/A | N/A | 10.5-13.5 Vdc | NDR | Adjust for 10.5-13.5 Vdc, select CCW rotation | FALSE
[24 empty] | 546 | M765N1015 | M9185D1004 | N/A | N/A | Q7130A1006 | 160° | N/A | 24 | 25 | 160 | 40 | N/A | N/A | N/A | 10.5-13.5 Vdc | NDR | Adjust for 10.5-13.5 Vdc, select CCW rotation | FALSE
[24 empty] | 547 | M765P1005 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 25 | 90 | 25 | N/A | N/A | N/A | 3.5 - 6.5 Vdc | NDR | 3 wire output | FALSE
[24 empty] | 548 | M765P1013 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 25 | 90 | 25 | N/A | N/A | N/A | 3.5 - 6.5 Vdc | NDR | 3 wire output | FALSE
[24 empty] | 549 | M765Q1004 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 25 | 90 | 25 | N/A | N/A | N/A | 0 - 1 mA | NDR | N/A | FALSE
[24 empty] | 550 | M7675A1001 | M9185D1004 | N/A | N/A | Q7630A1001 | 160 | N/A | 24 | 25 | 160 | 60 | N/A | 2 | N/A | 14-17 Vdc | NDR | N/A | FALSE
[24 empty] | 551 | M7675A1019 | M9185D1004 | 50017460-003 | N/A | Q7630A1001 | 90 | N/A | 120 | 25 | 90 | 30 | N/A | 2 | N/A | 14-17 Vdc | NDR | Trane | TRUE
[24 empty] | 552 | M7675G1008 | M9185D1004 | N/A | N/A | Q7630A1001 | 160 | N/A | 24 | 25 | 160 | 60 | N/A | 2 | N/A | 14-17 Vdc | NDR | N/A | TRUE
[24 empty] | 553 | M7682A1010 | M9185D1004 | N/A | N/A | Q7630A1001 | N/A | N/A | 24 | 60 | 160 | 60 | N/A | 1 | N/A | 14-17 Vdc | NDR | Includes Q209F1001 | TRUE
[24 empty] | 554 | M7685A1009 | M9185D1004 | N/A | N/A | Q7630A1001 | 160 | N/A | 24 | 60 | 160 | 60 | N/A | 2 | N/A | 14-17 Vdc | NDR | N/A | TRUE
[24 empty] | 555 | M7685A1017 | M9185D1004 | N/A | N/A | Q7630A1001 | 90 | N/A | 24 | 60 | 90 | 30 | N/A | 2 | YES | 14-17 Vdc | NDR | N/A | TRUE
[24 empty] | 556 | M7685A1025 | M9185D1004 | N/A | N/A | Q7630A1001 | 90 | N/A | 24 | 60 | 90 | 30 | N/A | 2 | N/A | 14-17 Vdc | NDR | N/A | TRUE
[24 empty] | 557 | M7685A1033 | M9185D1004 | 50017460-003 | N/A | Q7630A1001 | 160 | N/A | 120 | 60 | 160 | 60 | N/A | 2 | N/A | 14-17 Vdc | NDR | York | TRUE
[24 empty] | 558 | M7685A1041 | M9185D1004 | N/A | N/A | Q7630A1001 | 90 | N/A | 24 | 60 | 90 | 30 | N/A | 2 | N/A | 14-17 Vdc | NDR | Lennox | TRUE
[24 empty] | 559 | M7685G1006 | M9185D1004 | N/A | N/A | Q7630A1001 | 90 | N/A | 24 | 60 | 90 | 30 | N/A | 2 | N/A | 14-17 Vdc | NDR | Lennox | TRUE
[24 empty] | 560 | M7964A1001 | NDR | N/A | N/A | N/A | N/A | N/A | 120 | 35 | 90 | 30 | N/A | 2 | YES | Thermistor | NDR | N/A | TRUE
[24 empty] | 561 | M7964B1009 | NDR | N/A | N/A | N/A | N/A | N/A | 120 | 35 | 90 | 30 | N/A | 2 | YES | Thermistor | NDR | Nesbitt ITT | TRUE
[24 empty] | 562 | M7964B1017 | NDR | N/A | N/A | N/A | N/A | N/A | 120 | 35 | 160 | 60 | N/A | 2 | YES | Thermistor | NDR | Nesbitt ITT | TRUE
[24 empty] | 563 | M7964C1007 | NDR | N/A | N/A | N/A | N/A | N/A | 120 | 35 | 90 | 30 | N/A | 2 | YES | Thermistor | NDR | Nesbitt ITT | TRUE
[24 empty] | 564 | M7964C1015 | NDR | N/A | N/A | N/A | N/A | N/A | 120 | 35 | 90 | 30 | N/A | 2 | YES | Thermistor | NDR | N/A | TRUE
[24 empty] | 565 | M7964D1005 | N/A | N/A | N/A | N/A | N/A | N/A | 120 | 35 | 160 | 60 | N/A | 2 | N/A | 4-7 Vdc, 3-w | NDR | N/A | TRUE
[24 empty] | 566 | M7964D1013 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 35 | 160 | 60 | N/A | 2 | N/A | 4-7 Vdc, 3-w | NDR | N/A | TRUE
[24 empty] | 567 | M7975E1009 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 25 | 90 | 30 | N/A | 2 | N/A | 3.5-6 .5Vdc, 3-w | NDR | N/A | TRUE
[24 empty] | 568 | M7975E1017 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 25 | 90 | 30 | N/A | 2 | N/A | 3-6 Vdc, 3-w | NDR | N/A | TRUE
[24 empty] | 569 | M7983G1005 | N/A | N/A | N/A | N/A | N/A | N/A | 220 | 60 | 160 | 60 | N/A | 2 | N/A | n/a | NDR | IBM | TRUE
[24 empty] | 570 | M7984D1001 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 150 | 160 | 60 | N/A | 2 | N/A | 4-7 Vdc, 3-w | NDR | Includes 220741A | TRUE
[24 empty] | 571 | M7984N1008 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 150 | 90 | 30 | N/A | 2 | YES | 0-2.5 Vdc | NDR | Includes 220741A | TRUE
[24 empty] | 572 | M7985D1000 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 60 | 160 | 60 | N/A | 2 | N/A | 4-7 Vdc, 3-w | NDR | N/A | TRUE
[24 empty] | 573 | M805B1004 | M8185D1006 | N/A | N/A | N/A | 160° | N/A | 24 | 50 | 160 | 60 | N/A | N/A | N/A | Series 80 | M8185D1006 | N/A | TRUE
[24 empty] | 574 | M805B1012 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 27 | 160 | 120 | N/A | N/A | N/A | Series 80 | NDR | N/A | FALSE
[24 empty] | 575 | M805B1020 | M8185D1006 | N/A | N/A | N/A | 160° | N/A | 24 | 50 | 160 | 60 | N/A | N/A | N/A | Series 80 | M8185D1006 | N/A | FALSE
[24 empty] | 576 | M805B1038 | M8185D1006 | N/A | 220736A | N/A | 160° | N/A | 24 | 50 | 160 | 60 | 1 | N/A | N/A | Series 80 | NDR | N/A | FALSE
[24 empty] | 577 | M805C1003 | M8185D1006 | N/A | N/A | N/A | 160° | N/A | 24 | 50 | 160 | 60 | N/A | N/A | N/A | Series 80 | M8185D1006 | N/A | FALSE
[24 empty] | 578 | M805D1002 | M8185D1006 | N/A | N/A | N/A | 160° | N/A | 24 | 50 | 160 | 60 | N/A | N/A | N/A | Series 80 | M4185B1009 | Use auxiliary end of motor | FALSE
[24 empty] | 579 | M80AAA-3 | M6284D1000 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | M6284F1013 | Check voltage & stroke of motor | FALSE
[24 empty] | 580 | M80AAB-1 | M6284D1000 | N/A | 220736B | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | M6284F1013 | N/A | FALSE
[24 empty] | 581 | M80ACA-1 | M6285A1005 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | M6285A1005 | Check voltage & stroke of motor | FALSE
[24 empty] | 582 | M80ADA-1 | M6285A1005 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | M6285A1005 | Check voltage & stroke of motor | FALSE
[24 empty] | 583 | M80BAA-1 | M9184D1021 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | M9184A1019 | Check voltage & stroke of motor | FALSE
[24 empty] | 584 | M80BAA-4 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | M9184D1005 | Check voltage & stroke of motor | FALSE
[24 empty] | 585 | M80BCA-1 | M9185D1004 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | M9185D1004 | Check voltage & stroke of motor | FALSE
[24 empty] | 586 | M80BDA-1 | M9185D1004 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | M9185D1004 | Check voltage & stroke of motor | FALSE
[24 empty] | 587 | M80BEA-1 | M9185D1004 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | M9185A1018 | Check voltage & stroke of motor | FALSE
[24 empty] | 588 | M80FAA-2 | M9184D1021 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | M9184A1019 | Check voltage & stroke of motor | FALSE
[24 empty] | 589 | M80FCA-2 | M9185D1004 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | M9185D1004 | Check voltage & stroke of motor | FALSE
[24 empty] | 590 | M80FDA-1 | M9185D1004 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | M9185D1004 | Check voltage & stroke of motor | FALSE
[24 empty] | 591 | M80FEA-1 | M9185D1004 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | M9185A1018 | Check voltage & stroke of motor | FALSE
[24 empty] | 592 | M80FFA-1 | M9185D1004 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | M9185A1018 | Check voltage & stroke of motor | FALSE
[24 empty] | 593 | M80HAB-1 | M9184D1021 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | M9184F1034 | Check voltage & stroke of motor | FALSE
[24 empty] | 594 | M80HAC-1 | M9184D1021 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | M9184F1034 | Check voltage & stroke of motor | FALSE
[24 empty] | 595 | M80JAA--2 | M9184D1021 | N/A | N/A | N/A | ADJ | N/A | 24 | 150 | 65-240° | 60 | N/A | N/A | N/A | N/A | M9184A1019 | N/A | FALSE
[24 empty] | 596 | M80JAB--1 | M9184D1021 | N/A | 220736A | N/A | ADJ | N/A | 24 | 150 | 65-240° | 60 | 1 | N/A | N/A | N/A | M9184F1034 | N/A | FALSE
[24 empty] | 597 | M80JAC--1 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 150 | 65-240° | 60 | 2 | N/A | N/A | N/A | M9484E1017 | N/A | FALSE
[24 empty] | 598 | M80JCA--2 | M9185D1004 | N/A | N/A | N/A | ADJ | N/A | 24 | 50 | 65-180° | 60 | N/A | N/A | N/A | N/A | M9185A1018 | N/A | FALSE
[24 empty] | 599 | M80JCB--1 | M9185D1004 | N/A | 220736A | N/A | ADJ | N/A | 24 | 50 | 65-180° | 60 | 1 | N/A | N/A | N/A | M9185E1019 | N/A | FALSE
[24 empty] | 600 | M80JDA-1 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | NDR | N/A | FALSE
[24 empty] | 601 | M80JFA-1 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | NDR | N/A | FALSE
[24 empty] | 602 | M8175B1002 | M8185D1006 | N/A | 220736A | N/A | 160 | N/A | 24 | 25 | 160 | 60 | 1 | 2 | YES | Series 81 | NDR | N/A | FALSE
[24 empty] | 603 | M8182A1005 | M8185D1006 | N/A | N/A | N/A | 160 | N/A | 24 | 60 | 160 | 60 | N/A | 1 | N/A | Series 81 | M8185D1006 | N/A | TRUE
[24 empty] | 604 | M8182B1003 | M8185D1006 | N/A | 220736A | N/A | 160 | N/A | 24 | 60 | 160 | 60 | 1 | 1 | N/A | Series 81 | NDR | N/A | TRUE
[24 empty] | 605 | M8182B1011 | M8185D1006 | N/A | 220736A | 4074ERU | 160 | N/A | 24 | 60 | 160 | 60 | 1 | 1 | N/A | Series 81 | NDR | Includes weatherproof kit | TRUE
[24 empty] | 606 | M8185A1002 | M8185D1006 | N/A | N/A | N/A | 160 | N/A | 24 | 60 | 160 | 60 | N/A | 2 | N/A | Series 81 | M8185D1006 | N/A | TRUE
[24 empty] | 607 | M8185A1010 | M8185D1006 | N/A | N/A | N/A | N/A | N/A | 24 | 60 | 160 | 60 | N/A | 2 | N/A | Series 81 | M8185D1006 | N/A | TRUE
[24 empty] | 608 | M8185A1028 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 60 | 160 | 60 | N/A | 2 | N/A | Series 81 | NDR | N/A | TRUE
[24 empty] | 609 | M8185B1000 | M8185D1006 | N/A | 220736A | N/A | 160 | N/A | 24 | 60 | 160 | 60 | 1 | 2 | YES | Series 81 | NDR | N/A | TRUE
[24 empty] | 610 | M8185B1018 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 60 | 160 | 60 | 1 | 2 | N/A | Series 81 | M8185D1006 | N/A | TRUE
[24 empty] | 611 | M8185B1026 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 60 | 160 | 60 | 1 | 2 | N/A | Series 81 | NDR | N/A | TRUE
[24 empty] | 612 | M8185B1034 | M8185D1006 | N/A | 220736A | N/A | 160 | N/A | 24 | 60 | 160 | 60 | 1 | 2 | N/A | Series 81 | NDR | N/A | TRUE
[24 empty] | 613 | M8185D1006 | N/A | N/A | N/A | 220738A | ADJ | N/A | 24 | 60 | 90/160 | 30/60 | N/A | 2 | YES | Series 81 | N/A | TRADELINE | TRUE
[24 empty] | 614 | M8186G1008 | M8185D1006 | N/A | N/A | N/A | 160 | N/A | 24 | 60 | 160 | 60 | N/A | 2 | N/A | Series 81 | NDR | Includes auxiliary switch cams, use auxiliary shaft | TRUE
[24 empty] | 615 | M81AAA--12 | M6184D1035 | N/A | N/A | N/A | ADJ | N/A | 24 | 150 | 65-270° | 60 | N/A | N/A | N/A | N/A | M6184F1014 | N/A | TRUE
[24 empty] | 616 | M81AAA--13 | M6184D1035 | N/A | N/A | N/A | ADJ | N/A | 24 | 80 | 65-270° | 60 | N/A | N/A | N/A | N/A | M6184D1001 | N/A | FALSE
[24 empty] | 617 | M81AAB--5 | M6184D1035 | N/A | 220736A | N/A | ADJ | N/A | 24 | 150 | 65-270° | 60 | 1 | N/A | N/A | N/A | M6184F1015 | N/A | FALSE
[24 empty] | 618 | M81AAC-1 | M6184D1035 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | NDR | N/A | FALSE
[24 empty] | 619 | M81ACA-3 | M8185D1006 | N/A | N/A | N/A | 160° | N/A | 24 | 50 | 160° | 60 | N/A | N/A | N/A | N/A | M8185D1006 | N/A | FALSE
[24 empty] | 620 | M81ACB-1 | M8185D1006 | N/A | 220736A | N/A | 160° | N/A | 24 | 50 | 160° | 60 | 1 | N/A | N/A | N/A | NDR | N/A | FALSE
[24 empty] | 621 | M81ADA-2 | M8185D1006 | 50017460-001 | N/A | N/A | 160° | N/A | MULTI | 75 | 160° | 60 | N/A | N/A | N/A | N/A | M4185B1058 + 220736A | N/A | FALSE
[24 empty] | 622 | M81AEA-2 | M8185D1006 | 50017460-001 | N/A | N/A | 160° | N/A | MULTI | 75 | 160° | 60 | N/A | N/A | N/A | N/A | M4185B1009 | N/A | FALSE
[24 empty] | 623 | M81AFA-2 | M8185D1006 | N/A | N/A | N/A | 160° | N/A | 24 | 50 | 160° | 60 | N/A | N/A | N/A | N/A | NDR | N/A | FALSE
[24 empty] | 624 | M81AFB-1 | M8185D1006 | 50017460-001 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | M4185B1058 + 220736A | Check stroke and aux switch | FALSE
[24 empty] | 625 | M828A ALL | N/A | N/A | N/A | N/A | N/A | N/A | 120/240 | 25 | N/A | N/A | N/A | N/A | N/A | Series 80 | M836A1042 | N/A | FALSE
[24 empty] | 626 | M828B ALL | N/A | N/A | N/A | N/A | N/A | N/A | 120/240 | 25 | N/A | N/A | N/A | N/A | N/A | Series 80 | M836A1042 | N/A | FALSE
[24 empty] | 627 | M828C ALL | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 40 | N/A | N/A | N/A | N/A | N/A | Series 80 | M836A1042 | N/A | FALSE
[24 empty] | 628 | M828D ALL | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 40 | N/A | N/A | N/A | N/A | N/A | Series 80 | M836A1042 | N/A | FALSE
[24 empty] | 629 | M828X ALL | N/A | N/A | N/A | N/A | N/A | N/A | 120/208 | 25 | N/A | N/A | N/A | N/A | N/A | Series 80 | M836A1042 | N/A | FALSE
[24 empty] | 630 | M829A ALL | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 3 | 75° | N/A | 1 | N/A | N/A | Series 80 | NDR | N/A | FALSE
[24 empty] | 631 | M833A1007 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 6 | 90° | 15M | N/A | N/A | N/A | Series 80 | M833A1007 | N/A | FALSE
[24 empty] | 632 | M833A1015 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 6 | 90° | 15M | N/A | N/A | N/A | Series 80 | M833A1007 | N/A | TRUE
[24 empty] | 633 | M833A1023 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 6 | 90° | 15M | N/A | N/A | N/A | Series 80 | NDR | N/A | FALSE
[24 empty] | 634 | M833A1031 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 6 | 90° | 15M | N/A | N/A | N/A | Series 80 | M833A1007/U | N/A | FALSE
[24 empty] | 635 | M835A1002 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 4 | 80° | 80 | N/A | N/A | N/A | Series 80 | M835A1051 | N/A | FALSE
[24 empty] | 636 | M835A1010 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 4 | 80° | 80 | 1 | N/A | N/A | Series 80 | M835A1051 | N/A | FALSE
[24 empty] | 637 | M835A1028 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 4 | 80° | 80 | 1 | N/A | N/A | Series 80 | M835A1051 | N/A | FALSE
[24 empty] | 638 | M835A1036 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 4 | 80° | 80 | 1 | N/A | N/A | Series 80 | M835A1051 | N/A | FALSE
[24 empty] | 639 | M835A1044 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 4 | 80° | 80 | 1 | N/A | N/A | Series 80 | M835A1051 | N/A | FALSE
[24 empty] | 640 | M835A1051 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 4 | 80° | 80 | 1 | N/A | N/A | Series 80 | M835A1051 | N/A | FALSE
[24 empty] | 641 | M835A1069 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 4 | 80° | 80 | 1 | N/A | N/A | Series 80 | M835A1051 | N/A | FALSE
[24 empty] | 642 | M836A1000 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 20 | 80° | 30 | 1 | N/A | N/A | Series 80 | M836A1042 | N/A | FALSE
[24 empty] | 643 | M836A1018 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 20 | 75° | 30 | 1 | N/A | N/A | Series 80 | M836A1042 | N/A | FALSE
[24 empty] | 644 | M836A1026 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 20 | 75° | 50 | 1 | N/A | N/A | Series 80 | M836A1042 | N/A | FALSE
[24 empty] | 645 | M836A1034 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 20 | 75° | 30 | 1 | N/A | N/A | Series 80 | M836A1042 | N/A | FALSE
[24 empty] | 646 | M836A1042 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 20 | 75° | 30 | 1 | N/A | N/A | Series 80 | M836A1042 | N/A | FALSE
[24 empty] | 647 | M836A1059 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 20 | 75° | 50 | 1 | N/A | N/A | Series 80 | M836A1042 | N/A | FALSE
[24 empty] | 648 | M836A1067 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 20 | 75° | 30 | 1 | N/A | N/A | Series 80 | M836A1042 | N/A | FALSE
[24 empty] | 649 | M836A1075 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 20 | 75° | 30 | 1 | N/A | N/A | Series 80 | M836A1042 | N/A | FALSE
[24 empty] | 650 | M836B1009 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 15 | 75° | 25 | 1 | N/A | N/A | Series 80 | M836B1033 | N/A | FALSE
[24 empty] | 651 | M836B1017 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 15 | 75° | 25 | 1 | N/A | N/A | Series 80 | M836B1033 | N/A | FALSE
[24 empty] | 652 | M836B1025 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 15 | 75° | 25 | 1 | N/A | N/A | Series 80 | M836B1033 | N/A | FALSE
[24 empty] | 653 | M836B1033 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 15 | 75° | 25 | 1 | N/A | N/A | Series 80 | M836B1033 | N/A | FALSE
[24 empty] | 654 | M836B1041 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 15 | 75° | 25 | 1 | N/A | N/A | Series 80 | M836B1033 | N/A | FALSE
[24 empty] | 655 | M8405A1006 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 25 | 90° | 90 | N/A | N/A | N/A | SPST | M8405A1006 | N/A | FALSE
[24 empty] | 656 | M8405A1014 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 25 | 90° | 90 | N/A | N/A | N/A | SPST | M8405A1006 | N/A | TRUE
[24 empty] | 657 | M8405B1004 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 25 | 90° | 90 | N/A | N/A | N/A | SPST | NDR | N/A | FALSE
[24 empty] | 658 | M8414A1005 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 25 | 90° | 90 | 1 | N/A | N/A | SPST | M8414A1005 | N/A | FALSE
[24 empty] | 659 | M8415A1004 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 25 | 90° | 90 | 1 | N/A | N/A | SPST | M8415A1004 | N/A | FALSE
[24 empty] | 660 | M842A1008 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 6 | 90° | 18M | N/A | N/A | N/A | Series 80 | M842A1008 | N/A | FALSE
[24 empty] | 661 | M845A1001 | M8185D1006 | N/A | 220736A | N/A | 160° | N/A | 24 | 50 | 160 | 60 | 1 | N/A | N/A | Series 80 | NDR | N/A | FALSE
[24 empty] | 662 | M845A1027 | M8185D1006 | 50017460-001 | 220736A | N/A | 160° | N/A | MULTI | 50 | 160 | 60 | 1 | N/A | N/A | Series 80 | M4185B1058 + 220736A | N/A | FALSE
[24 empty] | 663 | M845A1035 | M8185D1006 | 50017460-001 | 220736A | N/A | 90° | N/A | MULTI | 50 | 90 | 30 | 1 | N/A | N/A | Series 80 | M4185B1058 | N/A | FALSE
[24 empty] | 664 | M845A1050 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 50 | 160 | 60 | 1 | N/A | N/A | Series 80 | NDR | UL555 refer to damper mfr. | FALSE
[24 empty] | 665 | M845A1068 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 50 | 160 | 60 | 1 | N/A | N/A | Series 80 | NDR | UL555 refer to damper mfr. | FALSE
[24 empty] | 666 | M845A4005 | M8185D1006 | 50017460-001 | 220736A | N/A | ADJ | N/A | MULTI | 50 | 90/160 | 30/60 | 1 | N/A | N/A | Series 80 | NDR | N/A | FALSE
[24 empty] | 667 | M845B1000 | M8185D1006 | N/A | 220736A | N/A | 160° | N/A | 24 | 50 | 160 | 60 | 1 | N/A | N/A | Series 80 | NDR | N/A | FALSE
[24 empty] | 668 | M845B1018 | M8185D1006 | 50017460-003 | 220736A | N/A | 160° | N/A | 120 | 50 | 160 | 60 | 1 | N/A | N/A | Series 80 | M4185B1058 + 220736A | N/A | FALSE
[24 empty] | 669 | M845B1026 | M8185D1006 | 50017460-001 | 220736A | N/A | 160° | N/A | 220 | 50 | 160 | 60 | 1 | N/A | N/A | Series 80 | NDR | N/A | FALSE
[24 empty] | 670 | M845C1009 | M8185D1006 | N/A | N/A | N/A | 160° | N/A | 24 | 50 | 160 | 60 | N/A | N/A | N/A | Series 80 | M8185D1006 | N/A | FALSE
[24 empty] | 671 | M845D1008 | M8185D1006 | N/A | N/A | N/A | 160° | N/A | 24 | 50 | 160 | 60 | N/A | N/A | N/A | Series 80 | NDR | N/A | FALSE
[24 empty] | 672 | M845D1016 | M8185D1006 | 50017460-003 | N/A | N/A | 160° | N/A | 120 | 50 | 160 | 60 | N/A | N/A | N/A | Series 80 | M4185B1058 + 220736A | N/A | FALSE
[24 empty] | 673 | M845D1024 | M8185D1006 | N/A | N/A | N/A | 160° | N/A | 24 | 50 | 160 | 60 | N/A | N/A | N/A | Series 80 | NDR | N/A | FALSE
[24 empty] | 674 | M845E1007 | M8185D1006 | 50017460-003 | 220736A | N/A | 160° | N/A | 120 | 50 | 160 | 60 | 1 | N/A | N/A | Series 80 | M4185B1009 | Use auxiliary end of motor | FALSE
[24 empty] | 675 | M845E4001 | M8185D1006 | 50017460-003 | 220736A | N/A | ADJ | N/A | 24/120 | 50 | 90/160 | 30/60 | 1 | N/A | N/A | Series 80 | M4185B1009 | Use auxiliary end of motor | FALSE
[24 empty] | 676 | M847A1008 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 2 | 45° | 20 | N/A | N/A | N/A | Series 80 | M847A1080 | N/A | FALSE
[24 empty] | 677 | M847A1023 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 2 | 45° | 20 | N/A | N/A | N/A | Series 80 | M847A1072 | N/A | FALSE
[24 empty] | 678 | M847A1031 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 2 | 45° | 20 | N/A | N/A | N/A | Series 80 | M847A1080 | N/A | FALSE
[24 empty] | 679 | M847A1049 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 2 | 45° | 20 | N/A | N/A | N/A | Series 80 | M847A1072 | N/A | FALSE
[24 empty] | 680 | M847A1056 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 2 | 45° | 20 | N/A | N/A | N/A | Series 80 | M847A1072 | N/A | FALSE
[24 empty] | 681 | M847A1064 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 2 | 45° | 20 | N/A | N/A | N/A | Series 80 | M847A1072 | N/A | FALSE
[24 empty] | 682 | M847A1072 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 2 | 45° | 20 | N/A | N/A | N/A | Series 80 | M847A1072 | N/A | FALSE
[24 empty] | 683 | M847A1080 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 2 | 45° | 20 | N/A | N/A | N/A | Series 80 | M847A1080 | N/A | TRUE
[24 empty] | 684 | M847A1098 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 2 | 45° | 20 | N/A | N/A | N/A | Series 80 | M847A1098 | N/A | FALSE
[24 empty] | 685 | M865A1009 | M8185D1006 | N/A | N/A | N/A | 160° | N/A | 24 | 25 | 160 | 40 | N/A | N/A | N/A | Series 80 | NDR | N/A | FALSE
[24 empty] | 686 | M865B1008 | M8185D1006 | N/A | 220736A | N/A | 160° | N/A | 24 | 25 | 160 | 40 | 1 | N/A | N/A | Series 80 | NDR | N/A | FALSE
[24 empty] | 687 | M904A1006 | M9184D1021 | N/A | N/A | N/A | 160° | N/A | 24 | 108 | 160 | 60 | N/A | N/A | N/A | 135 ohm | M9184A1019 | N/A | FALSE
[24 empty] | 688 | M904E1002 | M9184D1021 | N/A | N/A | N/A | 160° | N/A | 24 | 108 | 160 | 60 | N/A | N/A | N/A | 135 ohm | M9184A1019 | N/A | FALSE
[24 empty] | 689 | M904E1010 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 108 | 160 | 60 | N/A | N/A | N/A | 135 ohm | NDR | N/A | FALSE
[24 empty] | 690 | M904E1028 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 108 | 160 | 60 | N/A | N/A | N/A | 135 ohm | NDR | N/A | FALSE
[24 empty] | 691 | M904E1036 | M9184D1021 | N/A | N/A | Q181A1007 | 160° | N/A | 24 | 108 | 180 | 60 | N/A | N/A | N/A | 135 ohm | M9184A1019 | Q181: slaved motor application | FALSE
[24 empty] | 692 | M904E1051 | M9184D1021 | N/A | N/A | N/A | 90 | N/A | 24 | 108 | 90 | 30 | N/A | N/A | N/A | 135 ohm | NDR | N/A | FALSE
[24 empty] | 693 | M904E1085 | M9184D1021 | N/A | N/A | N/A | 90 | N/A | 24 | 108 | 90 | 30 | N/A | N/A | N/A | 135 ohm | NDR | Special cam for few positions | FALSE
[24 empty] | 694 | M904E1119 | M9194D1003 | N/A | N/A | N/A | 160 | N/A | 24 | 108 | 240 | 90 | N/A | N/A | N/A | 135 ohm | NDR | Tradeline is 90/160 degrees | FALSE
[24 empty] | 695 | M904E1150 | M9184D1021 | N/A | N/A | Q181A1007 | 160° | N/A | 24 | 108 | 160 | 240 | N/A | N/A | N/A | 135 ohm | M9194D1003 | Q181: slaved motor application | FALSE
[24 empty] | 696 | M904E1176 | M9184D1021 | N/A | N/A | Q181A1007 | 160° | N/A | 24 | 108 | 180 | 240 | N/A | N/A | N/A | 135 ohm | M9194D1003 | Q181: slaved motor application | FALSE
[24 empty] | 697 | M904E1218 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 108 | 160 | 240 | N/A | N/A | N/A | 135 ohm | NDR | N/A | FALSE
[24 empty] | 698 | M904E1226 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 14 | 160 | 7.5 | N/A | N/A | N/A | 135 ohm | NDR | N/A | FALSE
[24 empty] | 699 | M904E1234 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 38 | 180 | 15 | N/A | N/A | N/A | 135 ohm | NDR | For 30 sec 160° motor, Select M9184D1021 | FALSE
[24 empty] | 700 | M904E1242 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 38 | 180 | 15 | N/A | N/A | N/A | 135 ohm | NDR | For 30 sec 160° motor, Select M9184D1021 | FALSE
[24 empty] | 701 | M904E1267 | M9184D1021 | N/A | N/A | Q181A1007 | 160° | N/A | 24 | 54 | 160 | 30 | N/A | N/A | N/A | 135 ohm | M9184D1005 | Q181: slaved motor application | FALSE
[24 empty] | 702 | M904E1358 | M9184D1021 | N/A | N/A | Q181A1007 | 160° | N/A | 24 | 150 | 180 | 60 | N/A | N/A | N/A | 135 ohm | M9184A1019 | Q181: slaved motor application | FALSE
[24 empty] | 703 | M904E1366 | M9184D1021 | N/A | N/A | N/A | 90 | N/A | 24 | 150 | 90 | 30 | N/A | N/A | N/A | 135 ohm | M9184A1019 | N/A | FALSE
[24 empty] | 704 | M904E1374 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 150 | 160 | 60 | N/A | N/A | N/A | 135 ohm | NDR | N/A | FALSE
[24 empty] | 705 | M904F1001 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 37 | 160 | 15 | N/A | N/A | N/A | Series 62 | NDR | N/A | FALSE
[24 empty] | 706 | M904F1019 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 75 | 160 | 30 | N/A | N/A | N/A | Series 62 | NDR | N/A | FALSE
[24 empty] | 707 | M904F1027 | M6284D1000 | N/A | N/A | N/A | 160° | N/A | 24 | 150 | 160 | 60 |  | N/A | N/A | Series 62 | M6284D1000 | No internal balance circuit | FALSE
[24 empty] | 708 | M904F1035 | M6284D1000 | N/A | N/A | N/A | 160° | N/A | 24 | 150 | 160 | 60 | N/A | N/A | N/A | Series 62 | M6284D1000 | No internal balance circuit | FALSE
[24 empty] | 709 | M904F1043 | M6284D1000 | N/A | N/A | N/A | 90° | N/A | 24 | 150 | 90 | 30 | N/A | N/A | N/A | Series 62 | M6284F1013 | No internal balance circuit | FALSE
[24 empty] | 710 | M904F1050 | M6284D1000 | N/A | N/A | N/A | 160° | N/A | 24 | 150 | 160 | 240 | N/A | N/A | N/A | Series 62 | NDR | No internal balance circuit | FALSE
[24 empty] | 711 | M904G1000 | M6284D1000 | N/A | N/A | N/A | 160° | N/A | 24 | 150 | 160 | 60 | N/A | N/A | N/A | Series 62 | M6284D1000 | No internal balance circuit | FALSE
[24 empty] | 712 | M905E1009 | M9185D1004 | N/A | N/A | Q181A1007 | 160° | N/A | 24 | 50 | 160 | 60 | N/A | N/A | N/A | 135 ohm | M9185A1018 | Q181: slaved motor application | FALSE
[24 empty] | 713 | M905E1025 | M9185D1004 | N/A | N/A | Q181A1007 | 160° | N/A | 24 | 50 | 160 | 60 | N/A | N/A | N/A | 135 ohm | M9185A1018 | Q181: slaved motor application | FALSE
[24 empty] | 714 | M905E1058 | M9185D1004 | N/A | N/A | Q181A1007 | 160° | N/A | 24 | 50 | 160 | 60 | N/A | N/A | N/A | 135 ohm | M9185A1018 | Q181: slaved motor application | FALSE
[24 empty] | 715 | M905E1066 | M9185D1004 | N/A | N/A | Q181A1007 | 90° | N/A | 24 | 50 | 90 | 30 | N/A | N/A | N/A | 135 ohm | M9185A1018 | Q181: slaved motor application | FALSE
[24 empty] | 716 | M905E1074 | M9185D1004 | N/A | N/A | Q181A1007 | 160° | N/A | 24 | 50 | 160 | 60 | N/A | N/A | N/A | 135 ohm | M9185A1018 | Q181: slaved motor application | FALSE
[24 empty] | 717 | M905E1082 | M9185D1004 | N/A | N/A | Q181A1007 | 160° | N/A | 24 | 50 | 160 | 60 | N/A | N/A | N/A | 135 ohm | M9185A1018 | Q181: slaved motor application | FALSE
[24 empty] | 718 | M905E1108 | M9185D1004 | N/A | N/A | Q181A1007 | 160° | N/A | 24 | 50 | 160 | 60 | N/A | N/A | N/A | 135 ohm | M9185A1018 | Q181: slaved motor application | FALSE
[24 empty] | 719 | M905E1116 | M9185D1004 | N/A | N/A | Q181A1007 | 160° | N/A | 24 | 50 | 160 | 60 | N/A | N/A | N/A | 135 ohm | M9185A1018 | Q181: slaved motor application | FALSE
[24 empty] | 720 | M905E1124 | M9185D1004 | N/A | N/A | Q181A1007 | 160° | N/A | 24 | 50 | 160 | 60 | N/A | N/A | N/A | 135 ohm | M9185A1018 | Q181: slaved motor application | FALSE
[24 empty] | 721 | M905F1008 | M9185D1004 | N/A | N/A | N/A | 160° | N/A | 24 | 56 | 160 | 60 | N/A | N/A | N/A | 135 ohm | M9185A1018 | N/A | FALSE
[24 empty] | 722 | M905F1016 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 27 | 160 | 120 | N/A | N/A | N/A | 135 ohm | NDR | N/A | FALSE
[24 empty] | 723 | M905F1024 | M9185D1004 | N/A | N/A | N/A | 160° | N/A | 24 | 27 | 160 | 60 | N/A | N/A | N/A | 135 ohm | M9185A1018 | N/A | FALSE
[24 empty] | 724 | M905F1032 | M9185D1004 | N/A | N/A | N/A | 160° | N/A | 24 | 56 | 160 | 60 | N/A | N/A | N/A | 135 ohm | M9185A1018 | N/A | FALSE
[24 empty] | 725 | M905G1007 | M9185D1004 | N/A | N/A | N/A | 160° | N/A | 24 | 50 | 160 | 60 | N/A | N/A | N/A | 135 ohm | M9185A1018 | Use auxiliary end of motor | FALSE
[24 empty] | 726 | M905G1015 | M9185D1004 | N/A | N/A | N/A | 160° | N/A | 24 | 50 | 160 | 60 | N/A | N/A | N/A | 135 ohm | M9185A1018 | Use auxiliary end of motor | FALSE
[24 empty] | 727 | M905G1023 | M9185D1004 | N/A | N/A | N/A | 160° | N/A | 24 | 50 | 160 | 60 | N/A | N/A | N/A | 135 ohm | M9185A1018 | Use auxiliary end of motor | FALSE
[24 empty] | 728 | M905H1006 | M6285A1005 | N/A | N/A | N/A | 160° | N/A | 24 | 27 | 160 | 60 | N/A | N/A | N/A | Series 62 | M6285A1005 | Requires Q181 when using R927 | FALSE
[24 empty] | 729 | M905H1014 | M6285A1005 | N/A | N/A | N/A | 160° | N/A | 24 | 50 | 160 | 60 | N/A | N/A | N/A | Series 62 | M6285A1005 | Requires Q181 when using R927 | FALSE
[24 empty] | 730 | M905J1003 | M6285A1005 | N/A | N/A | N/A | 160° | N/A | 24 | 50 | 160 | 60 | N/A | N/A | N/A | Series 62 | M6285A1005 | Requires Q181 when using R927 | FALSE
[24 empty] | 731 | M905K1002 | M6285A1005 | N/A | N/A | N/A | 160° | N/A | 24 | 50 | 160 | 60 | N/A | N/A | N/A | Series 62 | M6285A1005 | Requires Q181 when using R927 | FALSE
[24 empty] | 732 | M905K1010 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 27 | 160 | 120 | N/A | N/A | N/A | Series 62 | NDR | N/A | FALSE
[24 empty] | 733 | M905L1001 | M6285A1005 | N/A | N/A | N/A | 160° | N/A | 24 | 50 | 160 | 60 | N/A | N/A | N/A | Series 62 | M6285A1005 | Use auxiliary end of motor, No internal balance circuit | FALSE
[24 empty] | 734 | M905L1019 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 27 | 160 | 120 | N/A | N/A | N/A | Series 62 | NDR | N/A | FALSE
[24 empty] | 735 | M905N1009 | M9185D1004 | N/A | N/A | N/A | 160° | N/A | 24 | 50 | 160 | 60 | N/A | N/A | N/A | 135 ohm | M9185C1006 | N/A | FALSE
[24 empty] | 736 | M905N1017 | M6285A1005 | N/A | N/A | N/A | 160° | N/A | 24 | 50 | 160 | 60 | N/A | N/A | N/A | 135 ohm | M9185C1006 | N/A | FALSE
[24 empty] | 737 | M905N1025 | M6285A1005 | N/A | N/A | N/A | 160° | N/A | 24 | 50 | 160 | 60 | N/A | N/A | N/A | 135 ohm | M9185C1006 | N/A | FALSE
[24 empty] | 738 | M905P1007 | M6285A1005 | N/A | N/A | N/A | 160° | N/A | 24 | 50 | 160 | 60 | N/A | N/A | N/A | Series 62 | M6285A1005 | No internal balance circuit | FALSE
[24 empty] | 739 | M905P1015 | M6285A1005 | N/A | N/A | N/A | 160° | N/A | 24 | 50 | 160 | 60 | N/A | N/A | N/A | Series 62 | M6285A1005 | No internal balance circuit | FALSE
[24 empty] | 740 | M9161A1008 | M9164D1009 | 50017460-003 | N/A | N/A | 160 | N/A | 120 | 35 | 160 | 60 | N/A | 1 | N/A | 135 ohm | M9164A1005 | N/A | FALSE
[24 empty] | 741 | M9161A1016 | M9164D1009 | N/A | N/A | N/A | 160 | N/A | 24 | 35 | 160 | 60 | N/A | 1 | N/A | 135 ohm | M9164A1005 | N/A | TRUE
[24 empty] | 742 | M9161A1024 | M9164A1005 | N/A | N/A | N/A | 90 | N/A | 120 | 35 | 90 | 30 | N/A | 1 | N/A | 135 ohm | M9164A1005 | N/A | TRUE
[24 empty] | 743 | M9161A1032 | M9164A1005 | N/A | N/A | N/A | 160 | N/A | 120 | 35 | 160 | 60 | N/A | 1 | N/A | 135 ohm | NDR | Carrier | TRUE
[24 empty] | 744 | M9161A1040 | M9184D1021 | 50017460-003 | N/A | N/A | 90 | N/A | 120 | 35 | 90 | 30 | N/A | 1 | N/A | 135 ohm | M9164A1005 | Includes weatherproof kit | TRUE
[24 empty] | 745 | M9161C1004 | M9164C1001 | N/A | 220736B | N/A | 160 | N/A | 24 | 35 | 160 | 60 | 2 | 1 | N/A | 135 ohm | M9164C1068 | N/A | TRUE
[24 empty] | 746 | M9161C1012 | M9164C1068 | N/A | N/A | N/A | 90 | N/A | 120 | 35 | 90 | 30 | 2 | 1 | N/A | 135 ohm | M9164C1068 | N/A | TRUE
[24 empty] | 747 | M9161V1009 | N/A | N/A | N/A | N/A | 160 | N/A | 24 | 35 | 160 | 60 | N/A | 1 | N/A | 135 ohm | NDR | Carrier | TRUE
[24 empty] | 748 | M9164A1005 | N/A | N/A | N/A | N/A | 90 | N/A | 120 | 35 | 90 | 30 | N/A | 2 | N/A | 135 ohm | N/A | N/A | TRUE
[24 empty] | 749 | M9164A1013 | N/A | N/A | N/A | N/A | 160 | N/A | 240 | 35 | 160 | 60 | N/A | 2 | N/A | 135 ohm | N/A | N/A | TRUE
[24 empty] | 750 | M9164A1021 | M9164A1005 | N/A | N/A | N/A | 160 | N/A | 120 | 35 | 160 | 60 | N/A | 2 | N/A | 135 ohm | M9164A1005 | N/A | TRUE
[24 empty] | 751 | M9164A1039 | M9164D1009 | 50017460-003 | N/A | N/A | 160 | N/A | 120 | 35 | 160 | 60 | N/A | 2 | N/A | 135 ohm | M9164A1005 | N/A | TRUE
[24 empty] | 752 | M9164A1047 | M9164D1009 | 50017460-001 | N/A | N/A | 160 | N/A | 220 | 35 | 160 | 60 | N/A | 2 | YES | 135 ohm | M9164A1013 | N/A | TRUE
[24 empty] | 753 | M9164A1054 | M9164D1009 | 50017460-003 | N/A | N/A | 90 | N/A | 120 | 35 | 90 | 30 | N/A | 2 | YES | 135 ohm | M9164A1005 | N/A | TRUE
[24 empty] | 754 | M9164A1062 | M9164D1009 | N/A | N/A | N/A | 90 | N/A | 24 | 35 | 90 | 30 | N/A | 2 | YES | 135 ohm | M9164A1005 | N/A | TRUE
[24 empty] | 755 | M9164A1070 | N/A | N/A | N/A | N/A | 160 | N/A | 24 | 35 | 160 | 60 | N/A | 2 | N/A | 135 ohm | N/A | N/A | TRUE
[24 empty] | 756 | M9164A1088 | M9164A1013 | N/A | N/A | N/A | 160 | N/A | 220 | 35 | 160 | 60 | N/A | 2 | N/A | 135 ohm | M9164A1013 | N/A | TRUE
[24 empty] | 757 | M9164A1096 | M9164D1009 | 50017460-003 | N/A | N/A | 160 | N/A | 120 | 35 | 160 | 60 | N/A | 2 | YES | 135 ohm | M9164A1005 | N/A | TRUE
[24 empty] | 758 | M9164A1104 | M9164D1009 | 50017460-003 | N/A | N/A | 160 | N/A | 120 | 35 | 160 | 60 | N/A | 2 | YES | 135 ohm | NDR | Carrier | TRUE
[24 empty] | 759 | M9164A1112 | M9164D1009 | 50017460-001 | N/A | N/A | 90 | N/A | MULTI | 35 | 90 | 30 | N/A | 2 | N/A | 135 ohm | NDR | York | TRUE
[24 empty] | 760 | M9164A1120 | M9164D1009 | N/A | N/A | N/A | 90 | N/A | 24 | 35 | 90 | 30 | N/A | 2 | N/A | 135 ohm | M9164A1005 | N/A | TRUE
[24 empty] | 761 | M9164A1138 | M9164D1009 | 50017460-003 | N/A | N/A | 160 | N/A | 120 | 35 | 160 | 60 | N/A | 2 | N/A | 135 ohm | NDR | Carrier | TRUE
[24 empty] | 762 | M9164B1003 | M9164D1009 | 50017460-003 | 220736A | N/A | 90 | 7 | 120 | 35 | 90 | 30 | 1 | 2 | N/A | 135 ohm | M9164C1068 | N/A | TRUE
[24 empty] | 763 | M9164C1001 | N/A | N/A | N/A | N/A | 160 | N/A | 24 | 35 | 160 | 60 | 2 | 2 | YES | 135 ohm | N/A | N/A | TRUE
[24 empty] | 764 | M9164C1019 | M9164D1009 | 50017460-003 | 220736B | N/A | 160 | N/A | 120 | 35 | 160 | 60 | 2 | 2 | YES | 135 ohm | M9164C1068 | N/A | TRUE
[24 empty] | 765 | M9164C1027 | M9164D1009 | 50017460-001 | 220736B | N/A | 160 | N/A | MULTI | 35 | 160 | 60 | 2 | 2 | YES | 135 ohm | NDR | N/A | TRUE
[24 empty] | 766 | M9164C1035 | M9164D1009 | 50017460-003 | 220736B | N/A | 90 | N/A | 120 | 35 | 90 | 30 | 2 | 2 | YES | 135 ohm | M9164C1068 | N/A | TRUE
[24 empty] | 767 | M9164C1043 | M9164D1009 | 50017460-003 | 220736B | N/A | 160 | N/A | 120 | 35 | 160 | 60 | 2 | 2 | YES | 135 ohm | M9164C1068 | N/A | TRUE
[24 empty] | 768 | M9164C1050 | M9164C1068 | N/A | N/A | N/A | 160 | N/A | 120 | 35 | 160 | 60 | 2 | 2 | N/A | 135 ohm | M9164C1068 | N/A | TRUE
[24 empty] | 769 | M9164C1068 | N/A | N/A | N/A | N/A | 90 | N/A | 120 | 35 | 90 | 30 | 2 | 2 | N/A | 135 ohm | N/A | N/A | TRUE
[24 empty] | 770 | M9164D1009 | N/A | N/A | N/A | N/A | ADJ | N/A | 24 | 35 | 90/160 | 30/60 | N/A | 2 | YES | 135 ohm | N/A | TRADELINE | TRUE
[24 empty] | 771 | M9164V1006 | N/A | N/A | N/A | N/A | 160 | N/A | 120 | 35 | 160 | 60 | N/A | 2 | N/A | 135 ohm | NDR | Carrier | TRUE
[24 empty] | 772 | M9164V1014 | M9164D1009 | N/A | N/A | N/A | 160 | N/A | 24 | 35 | 160 | 60 | N/A | 2 | N/A | 135 ohm | NDR | Carrier | TRUE
[24 empty] | 773 | M9164V1022 | M9164D1009 | N/A | N/A | Q209E1010 | 160 | N/A | 24 | 35 | 160 | 60 | N/A | 2 | N/A | 135 ohm | NDR | Carrier, with Q209E, crank arm | TRUE
[24 empty] | 774 | M9171A1006 | M9174D1007 | 50017460-003 | N/A | N/A | 160 | N/A | 120 | 75 | 160 | 60 | N/A | 1 | N/A | 135 ohm | M9174B1043 | N/A | TRUE
[24 empty] | 775 | M9171B1004 | M9184D1021 | 50017460-003 | 220736A | N/A | 160 | N/A | 120 | 75 | 160 | 60 | 1 | 1 | N/A | 135 ohm | M9174B1043 | N/A | TRUE
[24 empty] | 776 | M9171B1012 | M9174D1007 | 50017460-003 | 220736A | N/A | 90 | 10 | 120 | 75 | 90 | 30 | 1 | 1 | N/A | 135 ohm | M9174B1027 | N/A | TRUE
[24 empty] | 777 | M9171B1020 | NDR | N/A | N/A | N/A | N/A | N/A | 120 | 75 | 90 | 30 | 1 | 1 | N/A | 135 ohm | NDR | Cleaver Brooks | TRUE
[24 empty] | 778 | M9171C1002 | M9174C1025 | 50017460-003 | 220736B | N/A | 90 | 7 & 80 | 120 | 75 | 90 | 30 | 2 | 1 | N/A | 135 ohm | M9174C1025 | N/A | TRUE
[24 empty] | 779 | M9171C1010 | M9174D1007 | 50017460-003 | 220736B | N/A | N/A | 7 & 57 | 120 | 75 | 90 | 30 | 2 | 1 | N/A | 135 ohm | M9174C1041/U | Cleaver Brooks | TRUE
[24 empty] | 780 | M9172A1005 | M9185D1004 | N/A | N/A | N/A | 160 | N/A | 24 | 25 | 160 | 60 | N/A | 1 | N/A | 135 ohm | NDR | N/A | TRUE
[24 empty] | 781 | M9172A1013 | M9185D1004 | N/A | N/A | N/A | 160 | N/A | 24 | 25 | 160 | 60 | N/A | 1 | N/A | 135 ohm | NDR | N/A | TRUE
[24 empty] | 782 | M9172A1021 | M9185D1004 | N/A | N/A | N/A | 160 | N/A | 24 | 25 | 160 | 60 | N/A | 1 | N/A | 135 ohm | NDR | Carrier | TRUE
[24 empty] | 783 | M9172C1001 | M9185D1004 | N/A | 220736B | N/A | 160 | 35 & 35 | 24 | 25 | 160 | 60 | 2 | 1 | N/A | 135 ohm | NDR | Reznor | TRUE
[24 empty] | 784 | M9172W1004 | M9185D1004 | 50017460-003 | 220736A | Q209E1010 | 90 | 25 | 120 | 25 | 90 | 30 | 1 | 1 | N/A | 135 ohm | NDR | Trane, with Q209E1010 | TRUE
[24 empty] | 785 | M9172W1012 | N/A | N/A | N/A | N/A | 160 | 95 | 120 | 25 | 160 | 60 | 1 | 1 | N/A | 135 ohm | NDR | Carrier | TRUE
[24 empty] | 786 | M9174B1001 | M9174D1007 | 50017460-003 | 220736A | N/A | 160 | N/A | 120 | 75 | 160 | 60 | 1 | 2 | YES | 135 ohm | M9174B1043 | N/A | TRUE
[24 empty] | 787 | M9174B1019 | M9174D1007 | 50017460-003 | 220736A | N/A | 90 | N/A | 120 | 75 | 90 | 30 | 1 | 2 | YES | 135 ohm | M9174B1027 | N/A | TRUE
[24 empty] | 788 | M9174B1027 | N/A | N/A | N/A | N/A | 90 | N/A | 120 | 75 | 90 | 30 | 1 | 2 | N/A | 135 ohm | N/A | N/A | TRUE
[24 empty] | 789 | M9174B1035 | M9184D1021 | 50017460-003 | 220736A | N/A | N/A | 7 | 120 | 75 | 90 | 30 | 1 | 2 | N/A | 135 ohm | NDR | Cleaver Brooks | TRUE
[24 empty] | 790 | M9174B1043 | M9174B1027 | N/A | N/A | N/A | 160 | N/A | 120 | 75 | 160 | 60 | 1 | 2 | N/A | 135 ohm | M9174B1027 | N/A | TRUE
[24 empty] | 791 | M9174C1009 | M9174D1007 | 50017460-003 | 220736B | N/A | 160 | N/A | 120 | 75 | 160 | 60 | 2 | 2 | YES | 135 ohm | M9174C1033 | N/A | TRUE
[24 empty] | 792 | M9174C1017 | M9174D1007 | 50017460-003 | 220736B | N/A | 90 | 7 & 80 | 120 | 75 | 90 | 30 | 2 | 2 | YES | 135 ohm | M9174C1025 | N/A | TRUE
[24 empty] | 793 | M9174C1025 | N/A | N/A | N/A | N/A | 90 | 7 & 80 | 120 | 75 | 90 | 30 | 2 | 2 | N/A | 135 ohm | N/A | N/A | TRUE
[24 empty] | 794 | M9174C1033 | N/A | N/A | N/A | N/A | 160 | N/A | 120 | 75 | 160 | 60 | 2 | 2 | N/A | 135 ohm | N/A | N/A | TRUE
[24 empty] | 795 | M9174C1041 | N/A | N/A | N/A | N/A | N/A | 7 | 120 | 75 | 90 | 30 | 2 | 2 | N/A | 135 ohm | NDR | Cleaver Brooks | TRUE
[24 empty] | 796 | M9174D1007 | N/A | N/A | N/A | N/A | ADJ | N/A | 24 | 75 | 90/160 | 30/60 | N/A | 2 | YES | 135 ohm | N/A | TRADELINE | TRUE
[24 empty] | 797 | M9175A1002 | M9185D1004 | N/A | N/A | N/A | 160 | N/A | 24 | 25 | 160 | 60 | N/A | 2 | N/A | 135 ohm | NDR | N/A | TRUE
[24 empty] | 798 | M9175A1010 | M9185A1018 | N/A | N/A | 221455A | 90 | N/A | 24 | 25 | 90 | 30 | N/A | 2 | N/A | 135 ohm | NDR | Includes crank arm | TRUE
[24 empty] | 799 | M9175A1028 | M9185D1004 | N/A | N/A | N/A | 160 | N/A | 24 | 25 | 160 | 60 | N/A | 2 | N/A | 135 ohm | NDR | N/A | TRUE
[24 empty] | 800 | M9175A1036 | M9185D1004 | 50017460-003 | N/A | N/A | 90 | N/A | 120 | 25 | 90 | 30 | N/A | 2 | YES | 135 ohm | NDR | York | TRUE
[24 empty] | 801 | M9175A1044 | M9185D1004 | 50017460-003 | N/A | N/A | 90 | N/A | 120 | 25 | 90 | 30 | N/A | 2 | N/A | 135 ohm | NDR | N/A | TRUE
[24 empty] | 802 | M9175A1051 | M9185A1018 | N/A | N/A | N/A | 90 | N/A | 24 | 25 | 90 | 30 | N/A | 2 | N/A | 135 ohm | NDR | N/A | TRUE
[24 empty] | 803 | M9175A1069 | M9185D1004 | N/A | N/A | N/A | 160 | N/A | 24 | 25 | 160 | 60 | N/A | 2 | N/A | 135 ohm | NDR | Carrier | TRUE
[24 empty] | 804 | M9175A1077 | M9185D1004 | N/A | N/A | N/A | 90 | N/A | 24 | 25 | 90 | 30 | N/A | 2 | N/A | 135 ohm | NDR | Trane | TRUE
[24 empty] | 805 | M9175B1000 | N/A | N/A | N/A | N/A | 90 | 25 | 120 | 25 | 90 | 30 | 1 | 2 | N/A | 135 ohm | NDR | Trane | TRUE
[24 empty] | 806 | M9175C1008 | M9185D1004 | N/A | 220736B | N/A | 90 | 35 & 35 | 24 | 25 | 90 | 30 | 2 | 2 | N/A | 135 ohm | NDR | Reznor | TRUE
[24 empty] | 807 | M9175D1006 | M9185A1018 | 50017460-003 | N/A | N/A | ADJ | N/A | 120 | 25 | 90/160 | 30/60 | N/A | 2 | N/A | 135 ohm | M9185D1004 | N/A | TRUE
[24 empty] | 808 | M9175D1014 | M9185D1004 | N/A | N/A | 220738A | ADJ | N/A | 24 | 25 | 90/160 | 30/60 | N/A | 2 | YES | 135 ohm | M9185D1004 | TRADELINE | TRUE
[24 empty] | 809 | M9175V1003 | M9185D1004 | 50017460-003 | N/A | N/A | 90 | N/A | 120 | 25 | 90 | 30 | N/A | 2 | N/A | 135 ohm | NDR | Trane | TRUE
[24 empty] | 810 | M9175V1011 | NDR | N/A | N/A | N/A | N/A | N/A | 120 | 25 | 160 | 60 | N/A | 2 | N/A | 135 ohm | NDR | Carrier, leadwires | TRUE
[24 empty] | 811 | M9175W1001 | M9185D1004 | 50017460-003 | 220736A | N/A | 160 | 95 | 120 | 25 | 160 | 60 | 1 | 2 | N/A | 135 ohm | NDR | Carrier | TRUE
[24 empty] | 812 | M9175W1019 | M9185D1004 | 50017460-003 | 220736A | N/A | 90 | 25 | 120 | 25 | 90 | 30 | 1 | 2 | N/A | 135 ohm | NDR | Trane | TRUE
[24 empty] | 813 | M9175Y1007 | M9185D1004 | 50017460-003 | 220736B | N/A | 90 | 35 & 35 | 120 | 25 | 90 | 30 | 2 | 2 | N/A | 135 ohm | NDR | Trane | TRUE
[24 empty] | 814 | M9181A1004 | M9184D1021 | N/A | N/A | N/A | 160 | N/A | 24 | 150 | 160 | 60 | N/A | 1 | N/A | 135 ohm | M9184A1019 | Less junction box | TRUE
[24 empty] | 815 | M9181A1012 | M9184A1019 | N/A | N/A | N/A | 160 | N/A | 24 | 150 | 160 | 60 | N/A | 1 | N/A | 135 ohm | M9184A1019 | N/A | TRUE
[24 empty] | 816 | M9181A1020 | M9184D1021 | N/A | N/A | N/A | 160 | N/A | 24 | 150 | 160 | 60 | N/A | 1 | N/A | 135 ohm | M9184A1019 | N/A | TRUE
[24 empty] | 817 | M9181A1038 | M9184D1021 | N/A | N/A | N/A | 90 | N/A | 24 | 150 | 90 | 30 | N/A | 1 | N/A | 135 ohm | M9184A1019 | N/A | TRUE
[24 empty] | 818 | M9181B1002 | M9184D1021 | N/A | 220736A | N/A | 90 | 7 | 24 | 150 | 90 | 30 | 1 | 1 | N/A | 135 ohm | M9184C1031 | N/A | TRUE
[24 empty] | 819 | M9181B1010 | M9184D1021 | N/A | 220736A | N/A | 160 | N/A | 24 | 150 | 160 | 60 | 1 | 1 | N/A | 135 ohm | NDR | N/A | TRUE
[24 empty] | 820 | M9181B1028 | N/A | N/A | N/A | N/A | N/A | 7 | 24 | 150 | 90 | 30 | 1 | 1 | N/A | 135 ohm | NDR | Cleaver Brooks | TRUE
[24 empty] | 821 | M9181C1000 | N/A | N/A | N/A | N/A | N/A | 7 & 57 | 24 | 150 | 90 | 30 | 2 | 1 | N/A | 135 ohm | NDR | Cleaver Brooks | TRUE
[24 empty] | 822 | M9181D1008 | M9184D1021 | N/A | N/A | N/A | ADJ | N/A | 24 | 75 | 90/160 | 15/30 | N/A | 1 | N/A | 135 ohm | M9184D1005 | N/A | TRUE
[24 empty] | 823 | M9181D1016 | N/A | N/A | N/A | N/A | ADJ | N/A | 24 | 150 | 90/160 | 120/240 | N/A | 1 | N/A | 135 ohm | NDR | Trane | TRUE
[24 empty] | 824 | M9181D1024 | NDR | N/A | N/A | N/A | N/A | N/A | 24 | 150 | 90/160 | 60/120/240 | N/A | 1 | N/A | 135 ohm | NDR | Special Timing | TRUE
[24 empty] | 825 | M9182A1003 | M9185D1004 | N/A | N/A | N/A | 160 | N/A | 24 | 60 | 160 | 60 | N/A | 1 | N/A | 135 ohm | M9185A1018 | Less junction box | TRUE
[24 empty] | 826 | M9182A1011 | N/A | N/A | N/A | N/A | 160 | N/A | 24 | 60 | 160 | 60 | N/A | 1 | N/A | 135 ohm | N/A | N/A | TRUE
[24 empty] | 827 | M9182A1029 | M9185A1018 | N/A | N/A | N/A | 90 | N/A | 24 | 60 | 90 | 30 | N/A | 1 | N/A | 135 ohm | M9185A1018 | N/A | TRUE
[24 empty] | 828 | M9182A1037 | M9185D1004 | 50017460-003 | N/A | N/A | 90 | N/A | 120 | 60 | 90 | 30 | N/A | 1 | N/A | 135 ohm | NDR | Trane | TRUE
[24 empty] | 829 | M9182A1045 | M9185D1004 | N/A | N/A | N/A | 160 | N/A | 24 | 60 | 160 | 60 | N/A | 1 | N/A | 135 ohm | M9185A1018 | N/A | TRUE
[24 empty] | 830 | M9182A1052 | M9185A1018 | N/A | N/A | 4074ERU | 160 | N/A | 24 | 60 | 160 | 60 | N/A | 1 | N/A | 135 ohm | M9185A1018 | Includes weatherproof kit | TRUE
[24 empty] | 831 | M9182A1060 | M9185D1004 | 50017460-003 | N/A | N/A | 90 | N/A | 120 | 60 | 90 | 30 | N/A | 1 | YES | 135 ohm | NDR | York | TRUE
[24 empty] | 832 | M9182C1009 | M9185C1006 | N/A | N/A | N/A | 160 | N/A | 24 | 60 | 160 | 60 | 2 | 1 | N/A | 135 ohm | M9185C1006 | N/A | TRUE
[24 empty] | 833 | M9182C1017 | M9185D1004 | N/A | 220736B | N/A | 90 | N/A | 24 | 60 | 90 | 30 | 2 | 1 | N/A | 135 ohm | NDR | N/A | TRUE
[24 empty] | 834 | M9182D1007 | M9185D1004 | N/A | N/A | N/A | ADJ | N/A | 24 | 60 | 90/160 | 30/60 | N/A | 1 | N/A | 135 ohm | M9185D1004 | Less junction box | TRUE
[24 empty] | 835 | M9182D1015 | M9185D1004 | N/A | N/A | N/A | ADJ | N/A | 24 | 60 | 90/160 | 30/60 | N/A | 1 | N/A | 135 ohm | M9185D1004 | N/A | TRUE
[24 empty] | 836 | M9182D1023 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 60 | 90/160 | 60/120/240 | N/A | 1 | N/A | 135 ohm | NDR | Special Timing | TRUE
[24 empty] | 837 | M9182D1031 | M9185D1004 | 50017460-001 | N/A | Q209E1010 | ADJ | N/A | MULTI | 60 | 90/160 | 30/60 | N/A | 1 | N/A | 135 ohm | NDR | Includes Q209E | TRUE
[24 empty] | 838 | M9182D4001 | M9185D4008 | N/A | N/A | N/A | ADJ | N/A | 24 | 60 | 90/160 | 30/60 | N/A | 1 | N/A | 135 ohm | M9185D1004 | Canada | TRUE
[24 empty] | 839 | M9182W1002 | M9185D1004 | 50017460-003 | 220736A | Q209E1010 | 90 | 25 | 120 | 60 | 90 | 30 | 1 | 1 | N/A | 135 ohm | NDR | Trane, includes Q209E | TRUE
[24 empty] | 840 | M9183G1009 | M9185D1004 | N/A | N/A | N/A | 160 | N/A | 24 | 60 | 160 | 60 | N/A | 1 | N/A | 135 ohm | M9185A1018 | Use auxiliary shaft | TRUE
[24 empty] | 841 | M9184A1001 | M9184D1021 | N/A | N/A | N/A | 160 | N/A | 24 | 150 | 160 | 60 | N/A | 2 | N/A | 135 ohm | M9184A1019 | N/A | TRUE
[24 empty] | 842 | M9184A1019 | N/A | N/A | N/A | N/A | 160 | N/A | 24 | 150 | 160 | 60 | N/A | 2 | N/A | 135 ohm | N/A | N/A | TRUE
[24 empty] | 843 | M9184A1027 | M9184D1021 | N/A | N/A | N/A | 90 | N/A | 24 | 150 | 90 | 30 | N/A | 2 | YES | 135 ohm | M9184A1019 | N/A | TRUE
[24 empty] | 844 | M9184A1035 | M9184A1019 | N/A | N/A | N/A | 90 | N/A | 24 | 150 | 90 | 30 | N/A | 2 | N/A | 135 ohm | M9184A1019 | N/A | TRUE
[24 empty] | 845 | M9184A1043 | M9184D1021 | N/A | N/A | 220741A | 160 | N/A | 24 | 150 | 160 | 60 | N/A | 2 | YES | 135 ohm | M9184A1019 | Japan, with 220741A | TRUE
[24 empty] | 846 | M9184B1009 | N/A | N/A | N/A | N/A | N/A | 7 | 24 | 150 | 90 | 30 | 1 | 2 | N/A | 135 ohm | N/A | Cleaver Brooks | TRUE
[24 empty] | 847 | M9184B1017 | N/A | N/A | N/A | N/A | 90 | 7 | 24 | 150 | 90 | 30 | 1 | 2 | N/A | 135 ohm | N/A | N/A | TRUE
[24 empty] | 848 | M9184B1025 | N/A | N/A | N/A | N/A | N/A | 7 | 120 | 150 | 90 | 30 | 1 | 2 | N/A | 135 ohm | N/A | Cleaver Brooks | TRUE
[24 empty] | 849 | M9184B1033 | M9184D1021 | N/A | 220736A | N/A | 160 | N/A | 24 | 150 | 160 | 60 | 1 | 2 | N/A | 135 ohm | M9184F1034 | With tapped shaft | TRUE
[24 empty] | 850 | M9184B1041 | M9184D1021 | N/A | 220736A | 4074ERU | 90 | 7 | 24 | 150 | 90 | 30 | 1 | 2 | N/A | 135 ohm | M9184C1031 | Includes weatherproof kit | TRUE
[24 empty] | 851 | M9184C1007 | M9184D1021 | N/A | 220736B | N/A | 90 | 7 & 80 | 24 | 150 | 90 | 30 | 2 | 2 | YES | 135 ohm | M9184C1031 | With tapped shaft | TRUE
[24 empty] | 852 | M9184C1015 | M9184D1021 | N/A | 220736B | N/A | 160 | 7 & 80 | 24 | 150 | 160 | 60 | 2 | 2 | N/A | 135 ohm | NDR | With tapped shaft | TRUE
[24 empty] | 853 | M9184C1023 | N/A | N/A | N/A | N/A | N/A | 7 & 80 | 24 | 150 | 90 | 30 | 2 | 2 | N/A | 135 ohm | N/A | Cleaver Brooks | TRUE
[24 empty] | 854 | M9184C1031 | N/A | N/A | N/A | N/A | 90 | 7 & 80 | 24 | 150 | 90 | 30 | 2 | 2 | N/A | 135 ohm | N/A | With tapped shaft | TRUE
[24 empty] | 855 | M9184C1049 | N/A | N/A | N/A | N/A | N/A | 7 & 80 | 120 | 150 | 90 | 30 | 2 | 2 | N/A | 135 ohm | N/A | Cleaver Brooks | TRUE
[24 empty] | 856 | M9184D1005 | N/A | N/A | N/A | N/A | ADJ | N/A | 24 | 75 | 90/160 | 15/30 | N/A | 2 | N/A | 135 ohm | N/A | N/A | TRUE
[24 empty] | 857 | M9184D1013 | M9184D1021 | N/A | N/A | 220738A | ADJ | N/A | 24 | 150 | 90/160 | 30/60 | N/A | 2 | YES | 135 ohm | N/A | TRADELINE | TRUE
[24 empty] | 858 | M9184D1021 | N/A | N/A | N/A | N/A | ADJ | N/A | 24 | 150 | 90/160 | 30/60 | N/A | 2 | YES | 135 ohm | N/A | TRADELINE, with tapped shaft | TRUE
[24 empty] | 859 | M9184D1039 | M9184D1021 | N/A | N/A | 220741A | ADJ | N/A | 24 | 75 | 90/160 | 15/30 | N/A | 2 | YES | 135 ohm | M9184D1005 | Japan, includes 220741A | TRUE
[24 empty] | 860 | M9184D1047 | M9184D1021 | N/A | N/A | N/A | ADJ | N/A | 24 | 75 | 90/160 | 15/30 | N/A | 2 | N/A | 135 ohm | M9184D1005 | N/A | TRUE
[24 empty] | 861 | M9184D1054 | M9194D1003 | N/A | N/A | N/A | ADJ | N/A | 24 | 150 | 90/160 | 120/240 | N/A | 2 | YES | 135 ohm | M9194D1003 | N/A | TRUE
[24 empty] | 862 | M9184D1062 | M9184D1021 | N/A | N/A | N/A | ADJ | N/A | 24 | 150 | 90/160 | 30/60 | N/A | 2 | N/A | 135 ohm | M9184D1021 | N/A | TRUE
[24 empty] | 863 | M9184D4009 | N/A | N/A | N/A | N/A | ADJ | N/A | 24 | 150 | 90/160 | 30/60 | N/A | 2 | YES | 135 ohm | N/A | Canada, Tradeline | TRUE
[24 empty] | 864 | M9184E4006 | N/A | N/A | N/A | 220738A | ADJ | 120 | 24 | 150 | 90/160 | 30/60 | 1 | 2 | YES | 135 ohm | N/A | Canada, Tradeline, tapped shaft | TRUE
[24 empty] | 865 | M9184F1000 | M9184F1034 | N/A | N/A | N/A | ADJ | N/A | 24 | 150 | 90/160 | 30/60 | 2 | 2 | N/A | 135 ohm | M9184F1034 | N/A | TRUE
[24 empty] | 866 | M9184F1018 | M9184D1021 | N/A | 220736B | 220738A | ADJ | N/A | 24 | 150 | 90/160 | 30/60 | 2 | 2 | YES | 135 ohm | M9184F1034 | With tapped shaft | TRUE
[24 empty] | 867 | M9184F1026 | M9184D1021 | N/A | 220736B | 220741A | ADJ | N/A | 24 | 150 | 90/160 | 30/60 | 2 | 2 | YES | 135 ohm | M9184F1034 | Includes 220741A | TRUE
[24 empty] | 868 | M9184F1034 | N/A | N/A | N/A | N/A | ADJ | N/A | 24 | 150 | 90/160 | 30/60 | 2 | 2 | N/A | 135 ohm | N/A | With tapped shaft | TRUE
[24 empty] | 869 | M9185A1000 | M9185D1004 | N/A | N/A | N/A | 160 | N/A | 24 | 60 | 160 | 60 | N/A | 2 | N/A | 135 ohm | M9185A1018 | N/A | TRUE
[24 empty] | 870 | M9185A1018 | N/A | N/A | N/A | N/A | 160 | N/A | 24 | 60 | 160 | 60 | N/A | 2 | N/A | 135 ohm | N/A | N/A | TRUE
[24 empty] | 871 | M9185A1026 | M9185A1018 | N/A | N/A | N/A | 90 | N/A | 24 | 60 | 90 | 30 | N/A | 2 | N/A | 135 ohm | M9185A1018 | N/A | TRUE
[24 empty] | 872 | M9185A1034 | M9185D1004 | N/A | N/A | N/A | 160 | N/A | 24 | 60 | 160 | 60 | N/A | 2 | N/A | 135 ohm | M9185A1018 | N/A | TRUE
[24 empty] | 873 | M9185A1042 | M9185D1004 | 50017460-003 | N/A | N/A | 90 | N/A | 120 | 60 | 90 | 30 | N/A | 2 | N/A | 135 ohm | M9185A1018 | N/A | TRUE
[24 empty] | 874 | M9185A1059 | M9185D1004 | N/A | N/A | N/A | 90 | N/A | 24 | 60 | 90 | 30 | N/A | 2 | N/A | 135 ohm | NDR | Lennox | TRUE
[24 empty] | 875 | M9185A1067 | M9185D1004 | N/A | N/A | N/A | 90 | N/A | 24 | 60 | 90 | 30 | N/A | 2 | N/A | 135 ohm | NDR | York | TRUE
[24 empty] | 876 | M9185A1075 | N/A | N/A | N/A | N/A | 160 | N/A | 24 | 60 | 160 | 60 | N/A | 2 | YES | 135 ohm | N/A | Includes 220741A | TRUE
[24 empty] | 877 | M9185A1083 | M9185D1004 | N/A | N/A | N/A | 160 | N/A | 24 | 60 | 160 | 60 | N/A | 2 | N/A | 135 ohm | M9185A1018 | N/A | TRUE
[24 empty] | 878 | M9185A1091 | M9185D1004 | N/A | N/A | N/A | 90 | N/A | 24 | 60 | 90 | 30 | N/A | 2 | N/A | 135 ohm | M9185A1018 | Less junction box | TRUE
[24 empty] | 879 | M9185B1008 | M9185D1004 | 50017460-003 | 220736A | N/A | 90 | 30 | 120 | 60 | 90 | 30 | 1 | 2 | N/A | 135 ohm | NDR | N/A | TRUE
[24 empty] | 880 | M9185C1006 | N/A | N/A | N/A | N/A | 160 | N/A | 24 | 60 | 160 | 60 | 2 | 2 | N/A | 135 ohm | N/A | N/A | TRUE
[24 empty] | 881 | M9185C1014 | M9185D1004 | N/A | 220736B | N/A | 160 | N/A | 24 | 60 | 160 | 60 | 2 | 2 | N/A | 135 ohm | NDR | N/A | TRUE
[24 empty] | 882 | M9185C1022 | M9185D1004 | N/A | 220736B | N/A | 160 | N/A | 24 | 60 | 160 | 60 | 2 | 2 | N/A | 135 ohm | NDR | N/A | TRUE
[24 empty] | 883 | M9185D1004 | N/A | N/A | N/A | N/A | ADJ | N/A | 24 | 60 | 90/160 | 30/60 | N/A | 2 | YES | 135 ohm | N/A | TRADELINE | TRUE
[24 empty] | 884 | M9185D1012 | NDR | N/A | N/A | N/A | ADJ | N/A | 24 | 60 | 90/160 | 30/60 | N/A | 2 | N/A | 135 ohm | M9185D1004 | N/A | TRUE
[24 empty] | 885 | M9185D4008 | N/A | N/A | N/A | N/A | ADJ | N/A | 24 | 60 | 90/160 | 30/60 | N/A | 2 | YES | 135 ohm | N/A | Canada, Tradeline | TRUE
[24 empty] | 886 | M9185E1001 | M9185D1004 | N/A | 220736A | N/A | ADJ | 30 | 24 | 60 | 90/160 | 30/60 | 1 | 2 | YES | 135 ohm | M9185E1019 | N/A | TRUE
[24 empty] | 887 | M9185E1019 | N/A | N/A | N/A | N/A | ADJ | 30 | 24 | 60 | 90/160 | 30/60 | 1 | 2 | N/A | 135 ohm | N/A | N/A | TRUE
[24 empty] | 888 | M9185E4005 | N/A | N/A | N/A | N/A | ADJ | 120 | 24 | 60 | 90/160 | 30/60 | 1 | 2 | YES | 135 ohm | N/A | Canada, Tradeline, tapped shaft | TRUE
[24 empty] | 889 | M9185F1009 | N/A | N/A | N/A | N/A | N/A | 40 & 85 | 24 | 60 | 90/160 | 30/60 | 2 | 2 | N/A | 135 ohm | NDR | Carrier (W957G1006) | TRUE
[24 empty] | 890 | M9185W1017 | M9185D1004 | 50017460-003 | 220736A | Q209E1010 | 90 | 25 | 120 | 60 | 90 | 30 | 1 | 2 | N/A | 135 ohm | NDR | Trane , with Q209E | TRUE
[24 empty] | 891 | M9186G1006 | N/A | N/A | N/A | N/A | 160 | N/A | 24 | 60 | 160 | 60 | N/A | 2 | N/A | 135 ohm | N/A | Use auxiliary shaft | TRUE
[24 empty] | 892 | M9186G1014 | M9185D1004 | N/A | N/A | 220741A | 160 | N/A | 24 | 60 | 160 | 60 | N/A | 2 | YES | 135 ohm | M9185A1018 | Japan, includes 220741A, use auxiliary shaft | TRUE
[24 empty] | 893 | M9186G4000 | NDR | N/A | N/A | N/A | 160 | N/A | 24 | 60 | 160 | 60 | N/A | 2 | YES | 135 ohm | M9185E4005 or M9185D1004 | Canada, use auxiliary shaft, MAY WANT TO USE 220738A - BRACKET | TRUE
[24 empty] | 894 | M9191D1006 | M9194D1003 | N/A | N/A | N/A | ADJ | N/A | 24 | 300 | 90/160 | 120/240 | N/A | 1 | N/A | 135 ohm | M9194D1003 | N/A | TRUE
[24 empty] | 895 | M9191F1001 | N/A | N/A | N/A | N/A | ADJ | 7 & 57 | 24 | 300 | 90/160 | 120/240 | 2 | 1 | N/A | 135 ohm | N/A | N/A | TRUE
[24 empty] | 896 | M9194C1005 | N/A | N/A | N/A | N/A | 90 | 7 & 80 | 120 | 300 | 90 | 60 | 2 | 2 | N/A | 135 ohm | N/A | N/A | TRUE
[24 empty] | 897 | M9194D1003 | N/A | N/A | N/A | N/A | ADJ | N/A | 24 | 300 | 90/160 | 120/240 | N/A | 2 | YES | 135 ohm | N/A | TRADELINE | TRUE
[24 empty] | 898 | M9194D4007 | M9194D1003 | N/A | N/A | N/A | ADJ | N/A | 24 | 300 | 90/160 | 120/240 | N/A | 2 | YES | 135 ohm | M9194D1003 | Canada, Tradeline | TRUE
[24 empty] | 899 | M9194E1000 | N/A | N/A | N/A | N/A | ADJ | N/A | 24 | 300 | 90/160 | 120/240 | 1 | 2 | N/A | 135 ohm | N/A | N/A | TRUE
[24 empty] | 900 | M931A1009 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 108 | 90 | 30 | N/A | N/A | N/A | 135 ohm | M9484D1010 | N/A | TRUE
[24 empty] | 901 | M931A1017 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 108 | 90 | 60 | N/A | N/A | N/A | 135 ohm | NDR | N/A | FALSE
[24 empty] | 902 | M931A1025 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 150 | 160 | 60 | N/A | N/A | N/A | 135 ohm | M9484D1010 | N/A | FALSE
[24 empty] | 903 | M931A1033 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 37 | 160 | 15 | N/A | N/A | N/A | 135 ohm | NDR | N/A | FALSE
[24 empty] | 904 | M931A1041 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 54 | 90 | 15 | N/A | N/A | N/A | 135 ohm | M9484D1010 | N/A | FALSE
[24 empty] | 905 | M931A1058 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 75 | 160 | 30 | N/A | N/A | N/A | 135 ohm | M9484D1010 | N/A | FALSE
[24 empty] | 906 | M931A1066 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 108 | 90 | 30 | N/A | N/A | N/A | 135 ohm | M9484D1010 | N/A | FALSE
[24 empty] | 907 | M931A1074 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 108 | 160 | 60 | N/A | N/A | N/A | 135 ohm | M9484D1010 | N/A | FALSE
[24 empty] | 908 | M931A1082 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 108 | 90 | 60 | N/A | N/A | N/A | 135 ohm | NDR | N/A | FALSE
[24 empty] | 909 | M931A1090 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 150 | 160 | 240 | N/A | N/A | N/A | 135 ohm | NDR | N/A | FALSE
[24 empty] | 910 | M931A1108 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 150 | 90 | 60 | N/A | N/A | N/A | 135 ohm | NDR | N/A | FALSE
[24 empty] | 911 | M931A1116 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 150 | 90 | 30 | N/A | N/A | N/A | 135 ohm | M9484D1010 | N/A | FALSE
[24 empty] | 912 | M931A1124 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 108 | 90/160 | 30/60 | N/A | N/A | N/A | 135 ohm | M9494D1000 | N/A | FALSE
[24 empty] | 913 | M931A1132 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 108 | 90/160 | 60/120 | N/A | N/A | N/A | 135 ohm | M9484D1010 | N/A | FALSE
[24 empty] | 914 | M931A1140 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 150 | 90/160 | 30/60 | N/A | N/A | N/A | 135 ohm | M9484D1010 | N/A | FALSE
[24 empty] | 915 | M931A1157 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 37 | 90/160 | 7.5/15 | N/A | N/A | N/A | 135 ohm | NDR | N/A | FALSE
[24 empty] | 916 | M931A1165 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 76 | 90/160 | 15/30 | N/A | N/A | N/A | 135 ohm | M9484D1010 | N/A | FALSE
[24 empty] | 917 | M931A1173 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 108 | 90/160 | 30/60 | N/A | N/A | N/A | 135 ohm | M9484D1010 | N/A | FALSE
[24 empty] | 918 | M931A1181 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 108 | 90/160 | 120/240 | N/A | N/A | N/A | 135 ohm | NDR | N/A | FALSE
[24 empty] | 919 | M931A1199 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 54 | 90/160 | 30/60 | N/A | N/A | N/A | 135 ohm | M9484D1010 | N/A | FALSE
[24 empty] | 920 | M931A1207 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 150 | 160 | 60 | N/A | N/A | N/A | 135 ohm | M9484D1010 | N/A | FALSE
[24 empty] | 921 | M931A1215 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 108 | 90/160 | 30/60 | 1 | N/A | N/A | 135 ohm | M9484E1017 | N/A | FALSE
[24 empty] | 922 | M931A1223 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 108 | 90/160 | 60/120 | 1 | N/A | N/A | 135 ohm | NDR | N/A | FALSE
[24 empty] | 923 | M931A1231 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 108 | 90/160 | 30/60 | 1 | N/A | N/A | 135 ohm | M9484E1017 | N/A | FALSE
[24 empty] | 924 | M931A1249 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 27 | 90/160 | 7.5/15 | 1 | N/A | N/A | 135 ohm | NDR | N/A | FALSE
[24 empty] | 925 | M931A1256 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 54 | 90/160 | 15/30 | 1 | N/A | N/A | 135 ohm | M9484E1009 | N/A | FALSE
[24 empty] | 926 | M931A1264 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 108 | 90/160 | 30/60 | 1 | N/A | N/A | 135 ohm | M9484E1017 | N/A | FALSE
[24 empty] | 927 | M931A1272 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 108 | 90/160 | 120/240 | 1 | N/A | N/A | 135 ohm | NDR | N/A | FALSE
[24 empty] | 928 | M931A1280 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 150 | 90/160 | 30/60 | 1 | N/A | N/A | 135 ohm | M9484E1033 | N/A | FALSE
[24 empty] | 929 | M931A1298 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 150 | 90 | 60 | N/A | N/A | N/A | 135 ohm | NDR | N/A | FALSE
[24 empty] | 930 | M931A1306 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 108 | 90/160 | 30/60 | N/A | N/A | N/A | 135 ohm | M9484D1010 | N/A | FALSE
[24 empty] | 931 | M931A1314 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 108 | 90/160 | 60/120 | N/A | N/A | N/A | 135 ohm | M9494D1000 | N/A | FALSE
[24 empty] | 932 | M931A1322 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 108 | 90/160 | 30/60 | N/A | N/A | N/A | 135 ohm | M9484D1010 | N/A | FALSE
[24 empty] | 933 | M931A1330 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 150 | 160 | 60 | N/A | N/A | N/A | 135 ohm | NDR | N/A | FALSE
[24 empty] | 934 | M931B1008 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 108 | 90 | 30 | N/A | N/A | N/A | Series 62 | M6284F1013 | Requires Q181 when using R927 no internal balance circuit | FALSE
[24 empty] | 935 | M931B1016 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 150 | 90/160 | 30/60 | N/A | N/A | N/A | Series 62 | M6284F1013 | Requires Q181 when using R927 no internal balance circuit | FALSE
[24 empty] | 936 | M931B1024 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 150 | 160 | 60 | N/A | N/A | N/A | Series 62 | M6284D1000 | Requires Q181 when using R927 no internal balance circuit | FALSE
[24 empty] | 937 | M931B1032 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 150 | 160 | 30 | N/A | N/A | N/A | Series 62 | NDR | N/A | FALSE
[24 empty] | 938 | M931B1040 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 150 | 160 | 60 | N/A | N/A | N/A | Series 62 | M6284D1000 | Requires Q181 when using R927 no internal balance circuit | FALSE
[24 empty] | 939 | M931B1057 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 150 | 90 | 60 | N/A | N/A | N/A | Series 62 | NDR | N/A | FALSE
[24 empty] | 940 | M931C1007 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 108 | 90/160 | 30/60 | 1 | N/A | N/A | 135 ohm | M9484E1017 | N/A | FALSE
[24 empty] | 941 | M931C1015 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 150 | 90/160 | 60/120 | 1 | N/A | N/A | 135 ohm | NDR | N/A | FALSE
[24 empty] | 942 | M931C1023 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 150 | 90/160 | 30/60 | 1 | N/A | N/A | 135 ohm | M9484E1017 | N/A | FALSE
[24 empty] | 943 | M931C1031 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 37 | 90/160 | 7.5/15 | 1 | N/A | N/A | 135 ohm | NDR | N/A | FALSE
[24 empty] | 944 | M931C1049 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 75 | 90/160 | 15/30 | 1 | N/A | N/A | 135 ohm | M9484E1009 | N/A | FALSE
[24 empty] | 945 | M931C1056 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 150 | 90/160 | 120/240 | 1 | N/A | N/A | 135 ohm | NDR | N/A | FALSE
[24 empty] | 946 | M931C1064 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 150 | 90/160 | 30/60 | 1 | N/A | N/A | 135 ohm | M9484E1017 | N/A | FALSE
[24 empty] | 947 | M931C1072 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 150 | 90/160 | 30/60 | 1 | N/A | N/A | 135 ohm | M9484E1033 | N/A | FALSE
[24 empty] | 948 | M931D1006 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 150 | 160 | 60 | 1 | N/A | N/A | 135 ohm | M6284F1013 | No internal balance circuit | FALSE
[24 empty] | 949 | M931D1014 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 150 | 90 | 30 | 1 | N/A | N/A | 135 ohm | M6284F1013 | No internal balance circuit | FALSE
[24 empty] | 950 | M934A1003 | M9164D1009 | 50017460-001 | N/A | N/A | 160° | N/A | 240 | 35 | 160 | 60 | N/A | N/A | N/A | 135 ohm | NDR | N/A | FALSE
[24 empty] | 951 | M934A1011 | M9164D1009 | 50017460-003 | N/A | N/A | 160° | N/A | 120 | 35 | 160 | 60 | N/A | N/A | N/A | 135 ohm | NDR | N/A | FALSE
[24 empty] | 952 | M934A1029 | M9164D1009 | N/A | N/A | N/A | 160° | N/A | 24 | 35 | 160 | 60 | N/A | N/A | N/A | 135 ohm | M9164A1005 | N/A | FALSE
[24 empty] | 953 | M934A1037 | M9164D1009 | 50017460-001 | N/A | N/A | 160° | N/A | 220 | 35 | 160 | 60 | N/A | N/A | N/A | 135 ohm | M9164A1013 | N/A | FALSE
[24 empty] | 954 | M934A1045 | M9164D1009 | N/A | 220736B | N/A | 160° | N/A | 24 | 35 | 160 | 60 | 2 | N/A | N/A | 135 ohm | M9164C1068 | N/A | FALSE
[24 empty] | 955 | M934A1052 | M9164D1009 | 50017460-003 | 220736B | N/A | 160° | N/A | 120 | 35 | 160 | 60 | 2 | N/A | N/A | 135 ohm | M9164C1068 | N/A | FALSE
[24 empty] | 956 | M934A1060 | M9164D1009 | 50017460-001 | 220736B | N/A | 160° | N/A | 240 | 35 | 160 | 60 | 2 | N/A | N/A | 135 ohm | NDR | N/A | FALSE
[24 empty] | 957 | M934A1078 | M9164D1009 | 50017460-001 | 220736B | N/A | 160° | N/A | 220 | 35 | 160 | 60 | 2 | N/A | N/A | 135 ohm | NDR | N/A | FALSE
[24 empty] | 958 | M934A1086 | M9164D1009 | 50017460-003 | N/A | N/A | 160° | N/A | 120 | 35 | 160 | 60 | N/A | N/A | N/A | 135 ohm | M9164A1005 | N/A | FALSE
[24 empty] | 959 | M934A1094 | M9164D1009 | 50017460-003 | 220736B | N/A | 160° | N/A | 120 | 35 | 160 | 60 | 2 | N/A | N/A | 135 ohm | M9164C1068 | N/A | FALSE
[24 empty] | 960 | M934A1102 | M9164D1009 | 50017460-001 | N/A | N/A | 90° | N/A | 240 | 35 | 90 | 35 | N/A | N/A | N/A | 135 ohm | NDR | N/A | FALSE
[24 empty] | 961 | M934A1128 | M9164D1009 | 50017460-003 | 220736B | N/A | 90° | N/A | 120 | 35 | 90 | 35 | 2 | N/A | N/A | 135 ohm | M9164C1068 | N/A | FALSE
[24 empty] | 962 | M934A1136 | M9164D1009 | 50017460-003 | N/A | N/A | 90° | N/A | 120 | 35 | 90 | 35 | N/A | N/A | N/A | 135 ohm | M9164A1005 | N/A | FALSE
[24 empty] | 963 | M934A1144 | M9164D1009 | N/A | N/A | N/A | 90° | N/A | 24 | 35 | 90 | 35 | N/A | N/A | N/A | 135 ohm | NDR | N/A | FALSE
[24 empty] | 964 | M934A1169 | M9164D1009 | N/A | N/A | N/A | 160° | N/A | 24 | 35 | 160 | 60 | N/A | N/A | N/A | 135 ohm | M9164A1005 | N/A | FALSE
[24 empty] | 965 | M934A1193 | M9164D1009 | N/A | 220736B | N/A | 160° | N/A | 24 | 35 | 160 | 60 | 2 | N/A | N/A | 135 ohm | M9164C1068 | N/A | FALSE
[24 empty] | 966 | M934A1201 | M9164D1009 | 50017460-001 | N/A | N/A | 160° | N/A | 240 | 35 | 160 | 60 | N/A | N/A | N/A | 135 ohm | M9164A1013 | N/A | FALSE
[24 empty] | 967 | M934A1219 | M9164D1009 | 50017460-003 | N/A | N/A | 160° | N/A | 120 | 35 | 160 | 60 | N/A | N/A | N/A | 135 ohm | M9164A1005 | N/A | FALSE
[24 empty] | 968 | M934A1227 | M9164D1009 | N/A | N/A | N/A | 160° | N/A | 24 | 35 | 160 | 60 | N/A | N/A | N/A | 135 ohm | M9164D1009 | N/A | FALSE
[24 empty] | 969 | M934A1235 | M9164D1009 | 50017460-001 | N/A | N/A | 160° | N/A | 220 | 35 | 160 | 60 | N/A | N/A | N/A | 135 ohm | M9164A1013 | N/A | FALSE
[24 empty] | 970 | M934A1243 | M9164D1009 | N/A | 220736B | N/A | 160° | N/A | 24 | 35 | 160 | 60 | 2 | N/A | N/A | 135 ohm | M9164C1068 | N/A | FALSE
[24 empty] | 971 | M934A1250 | M9164D1009 | 50017460-003 | 220736B | N/A | 160° | N/A | 120 | 35 | 160 | 60 | 2 | N/A | N/A | 135 ohm | M9164C1068 | N/A | FALSE
[24 empty] | 972 | M934A1268 | M9164D1009 | 50017460-001 | 220736B | N/A | 160° | N/A | 240 | 35 | 160 | 60 | 2 | N/A | N/A | 135 ohm | NDR | N/A | FALSE
[24 empty] | 973 | M934A1276 | M9164D1009 | 50017460-001 | 220736B | N/A | 160° | N/A | 220 | 35 | 160 | 60 | 2 | N/A | N/A | 135 ohm | NDR | N/A | FALSE
[24 empty] | 974 | M934A1284 | M9164D1009 | 50017460-003 | N/A | N/A | 160° | N/A | 120 | 35 | 160 | 60 | N/A | N/A | N/A | 135 ohm | M9164A1005 | N/A | FALSE
[24 empty] | 975 | M934A1292 | M9164D1009 | 50017460-003 | 220736B | N/A | 160° | N/A | 120 | 35 | 160 | 60 | 2 | N/A | N/A | 135 ohm | M9164C1068 | N/A | FALSE
[24 empty] | 976 | M934A1300 | M9164D1009 | 50017460-001 | N/A | N/A | 90° | N/A | 240 | 35 | 90 | 30 | N/A | N/A | N/A | 135 ohm | NDR | N/A | FALSE
[24 empty] | 977 | M934A1318 | M9164D1009 | 50017460-003 | 220736B | N/A | 90° | N/A | 120 | 35 | 90 | 30 | 2 | N/A | N/A | 135 ohm | M9164C1068 | N/A | FALSE
[24 empty] | 978 | M934A1326 | M9164D1009 | 50017460-003 | N/A | N/A | 90° | N/A | 120 | 35 | 90 | 30 | N/A | N/A | N/A | 135 ohm | M9164A1005 | N/A | FALSE
[24 empty] | 979 | M934A1334 | M9164D1009 | N/A | N/A | N/A | 90° | N/A | 24 | 35 | 90 | 30 | N/A | N/A | N/A | 135 ohm | NDR | N/A | FALSE
[24 empty] | 980 | M934A1342 | M9164D1009 | N/A | N/A | N/A | 160° | N/A | 24 | 35 | 160 | 60 | N/A | N/A | N/A | 135 ohm | M9164A1005 | N/A | FALSE
[24 empty] | 981 | M934A1359 | M9164D1009 | N/A | 220736B | N/A | 160° | N/A | 24 | 35 | 160 | 60 | 2 | N/A | N/A | 135 ohm | M9164C1068 | N/A | FALSE
[24 empty] | 982 | M934A1367 | M9164D1009 | 50017460-003 | N/A | Q209E1010 | 160° | N/A | 120 | 35 | 160 | 60 | N/A | N/A | N/A | 135 ohm | NDR | Carrier Special | FALSE
[24 empty] | 983 | M934A1375 | M9164D1009 | 50017460-001 | N/A | N/A | 160° | N/A | 240 | 35 | 160 | 60 | N/A | N/A | N/A | 135 ohm | NDR | N/A | FALSE
[24 empty] | 984 | M934A1383 | M9164D1009 | 50017460-001 | N/A | N/A | 160° | N/A | 240 | 35 | 160 | 60 | N/A | N/A | N/A | 135 ohm | M9164A1013 | N/A | FALSE
[24 empty] | 985 | M934A1391 | M9164D1009 | 50017460-003 | N/A | N/A | 90° | N/A | 120 | 35 | 90 | 35 | N/A | N/A | N/A | 135 ohm | M9164A1005 | N/A | FALSE
[24 empty] | 986 | M934A1409 | M9164D1009 | N/A | N/A | N/A | 90° | N/A | 24 | 35 | 90 | 35 | N/A | N/A | N/A | 135 ohm | NDR | N/A | FALSE
[24 empty] | 987 | M934A1425 | M9164D1009 | N/A | N/A | N/A | 160° | N/A | 24 | 35 | 160 | 60 | N/A | N/A | N/A | 135 ohm | M9164A1005 | N/A | FALSE
[24 empty] | 988 | M934A1433 | M9164D1009 | 50017460-001 | 220736B | N/A | 160° | N/A | 240 | 35 | 160 | 60 | 2 | N/A | N/A | 135 ohm | NDR | N/A | FALSE
[24 empty] | 989 | M934A1441 | M9164D1009 | 50017460-003 | N/A | N/A | 160° | N/A | 120 | 35 | 160 | 60 | N/A | N/A | N/A | 135 ohm | M9164A1005 | N/A | FALSE
[24 empty] | 990 | M934A1458 | M9164D1009 | N/A | N/A | N/A | 90° | N/A | 24 | 35 | 90 | 35 | N/A | N/A | N/A | 135 ohm | NDR | N/A | FALSE
[24 empty] | 991 | M934A1466 | M9164D1009 | N/A | N/A | N/A | 90° | N/A | 24 | 35 | 90 | 35 | N/A | N/A | N/A | 135 ohm | NDR | N/A | FALSE
[24 empty] | 992 | M934A1474 | M9164D1009 | N/A | 220736B | N/A | 160° | N/A | 24 | 35 | 160 | 60 | 2 | N/A | N/A | 135 ohm | M9164C1068 | N/A | FALSE
[24 empty] | 993 | M934A1482 | M9164D1009 | 50017460-003 | 220736B | N/A | 160° | N/A | 120 | 35 | 160 | 60 | 2 | N/A | N/A | 135 ohm | M9164C1068 | N/A | FALSE
[24 empty] | 994 | M934A1490 | M9164D1009 | N/A | N/A | Q209E1010 | 160° | N/A | 24 | 35 | 160 | 60 | N/A | N/A | N/A | 135 ohm | NDR | Carrier Special | FALSE
[24 empty] | 995 | M934A1508 | M9164D1009 | 50017460-001 | N/A | N/A | 160° | N/A | 240 | 35 | 160 | 60 | N/A | N/A | N/A | 135 ohm | NDR | N/A | FALSE
[24 empty] | 996 | M934A1516 | M9164D1009 | 50017460-003 | 220736A | N/A | 90° | N/A | 120 | 35 | 90 | 35 | 1 | N/A | N/A | 135 ohm | M9164C1068 | N/A | FALSE
[24 empty] | 997 | M934A1524 | M9164D1009 | N/A | N/A | N/A | 160° | N/A | 24 | 35 | 160 | 60 | N/A | N/A | N/A | 135 ohm | M9164A1005 | N/A | FALSE
[24 empty] | 998 | M934A1532 | M9164D1009 | 50017460-001 | N/A | N/A | 90° | N/A | 240 | 35 | 90 | 35 | N/A | N/A | N/A | 135 ohm | NDR | N/A | FALSE
[24 empty] | 999 | M934A1540 | M9164D1009 | 50017460-003 | N/A | N/A | 90° | N/A | 120 | 35 | 90 | 35 | N/A | N/A | N/A | 135 ohm | M9164A1005 | N/A | FALSE
[24 empty] | 1000 | M934A1557 | M9164D1009 | 50017460-001 | N/A | N/A | 160° | N/A | 208/240 | 35 | 160 | 60 | N/A | N/A | N/A | 135 ohm | NDR | N/A | FALSE
[24 empty] | 1001 | M934A1565 | M9164D1009 | 50017460-003 | 220736A | N/A | 90° | N/A | 120 | 35 | 90 | 35 | 1 | N/A | N/A | 135 ohm | M9164C1068 | Reset auxiliary switch | FALSE
[24 empty] | 1002 | M934A1573 | M9164D1009 | 50017460-003 | N/A | N/A | 160° | N/A | 120 | 35 | 160 | 60 | N/A | N/A | N/A | 135 ohm | M9164A1005 | Carrier Special | FALSE
[24 empty] | 1003 | M934A1599 | M9164D1009 | N/A | N/A | Q209E1010 | 160° | N/A | 24 | 35 | 160 | 60 | N/A | N/A | N/A | 135 ohm | NDR | Carrier Special | FALSE
[24 empty] | 1004 | M934B1036 | M6284D1000 | N/A | N/A | N/A | 90° | N/A | 24 | 35 | 90 | 35 | N/A | N/A | N/A | Series 62 | M6284F1013 | No internal balance circuit, requires Q181 when using R927 | FALSE
[24 empty] | 1005 | M934C1001 | M9164D1009 | 50017460-003 | N/A | Q181A1007 | 90° | N/A | 120 | 35 | 90 | 35 | N/A | N/A | N/A | 135 ohm | M9164A1005 | Q181 for Nesbitt Relay Driver | FALSE
[24 empty] | 1006 | M934D1000 | M9174D1007 | 50017460-003 | 220736A | N/A | 160° | N/A | 120 | 75 | 160 | 60 | 1 | N/A | N/A | 135 ohm | M9174B1043 | N/A | FALSE
[24 empty] | 1007 | M934D1018 | M9174D1007 | 50017460-003 | 220736B | N/A | 160° | N/A | 120 | 75 | 160 | 60 | 2 | N/A | N/A | 135 ohm | M9174C1033 | N/A | FALSE
[24 empty] | 1008 | M934D1026 | M9174D1007 | 50017460-003 | 220736A | N/A | 90° | N/A | 120 | 75 | 90 | 35 | 1 | N/A | N/A | 135 ohm | M9174B1027 | N/A | FALSE
[24 empty] | 1009 | M934D1034 | M9174D1007 | 50017460-003 | 220736B | N/A | 90° | N/A | 120 | 75 | 90 | 35 | 2 | N/A | N/A | 135 ohm | M9174C1025 | N/A | FALSE
[24 empty] | 1010 | M934D1042 | M9174D1007 | 50017460-003 | 220736B | N/A | 90° | N/A | 120 | 75 | 90 | 35 | 2 | N/A | N/A | 135 ohm | NDR | Cleaver Brooks Special | FALSE
[24 empty] | 1011 | M934D1059 | M9174D1007 | 50017460-003 | 220736A | N/A | 90° | N/A | 120 | 75 | 90 | 35 | 1 | N/A | N/A | 135 ohm | NDR | Cleaver Brooks Special | FALSE
[24 empty] | 1012 | M934E1009 | M9174D1007 | N/A | N/A | N/A | 160° | N/A | 24 | 75 | 160 | 60 | N/A | N/A | N/A | 135 ohm | M9174B1043 | N/A | FALSE
[24 empty] | 1013 | M934E1017 | M9174D1007 | 50017460-003 | N/A | N/A | 160° | N/A | 120 | 75 | 160 | 60 | N/A | N/A | N/A | 135 ohm | M9174B1043 | N/A | FALSE
[24 empty] | 1014 | M934E1025 | M9174D1007 | 50017460-003 | N/A | N/A | 90° | N/A | 120 | 75 | 90 | 35 | N/A | N/A | N/A | 135 ohm | M9174B1043 | N/A | FALSE
[24 empty] | 1015 | M941A1008 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 75 | 90/160 | 15/30 | N/A | N/A | N/A | 135 ohm | M9484D1010 | N/A | FALSE
[24 empty] | 1016 | M941A1016 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 150 | 90/160 | 30/60 | N/A | N/A | N/A | 135 ohm | M9484D1010 | Tapped aux shaft | FALSE
[24 empty] | 1017 | M941A1024 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 150 | 90/160 | 60/120 | N/A | N/A | N/A | 135 ohm | M9484D1010 | N/A | FALSE
[24 empty] | 1018 | M941A1032 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 150 | 90/160 | 30/60 | N/A | N/A | N/A | 135 ohm | M9484D1010 | Tapped aux shaft | FALSE
[24 empty] | 1019 | M941A1040 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 37 | 90/160 | 7.5/15 | N/A | N/A | N/A | 135 ohm | NDR | N/A | FALSE
[24 empty] | 1020 | M941A1057 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 75 | 90/160 | 15/30 | N/A | N/A | N/A | 135 ohm | M9484D1010 | N/A | FALSE
[24 empty] | 1021 | M941A1065 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 75 | 90/160 | 15/30 | N/A | N/A | N/A | 135 ohm | M9484D1010 | N/A | FALSE
[24 empty] | 1022 | M941A1073 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 150 | 90/160 | 30/60 | N/A | N/A | N/A | 135 ohm | M9484D1010 | Tapped aux shaft | FALSE
[24 empty] | 1023 | M941A1081 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 150 | 90/160 | 30/60 | N/A | N/A | N/A | 135 ohm | M9484D1010 | Tapped aux shaft | FALSE
[24 empty] | 1024 | M941A1099 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 150 | 90/160 | 60/120 | N/A | N/A | N/A | 135 ohm | M9494D1000 | N/A | FALSE
[24 empty] | 1025 | M941A1107 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 37 | 90/160 | 7.5/15 | N/A | N/A | N/A | 135 ohm | NDR | N/A | FALSE
[24 empty] | 1026 | M941A4002 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 150 | 90/160 | 30/60 | N/A | N/A | N/A | 135 ohm | M9484D1010 | Tapped aux shaft | FALSE
[24 empty] | 1027 | M941B1007 | N/A | N/A | N/A | N/A | N/A | ADJ | 24 | 150 | 90/160 | 30/60 | N/A | N/A | N/A | Series 62 | M6284F1013 | No internal balance circuit | FALSE
[24 empty] | 1028 | M941B1015 | M6284D1000 | N/A | N/A | N/A | N/A | ADJ | 24 | 50 | 90/160 | 30/60 | N/A | N/A | N/A | Series 62 | NDR | No internal balance circuit | FALSE
[24 empty] | 1029 | M941C1006 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 75 | 90/160 | 15/30 | 1 | N/A | N/A | 135 ohm | M9484E1009 | N/A | FALSE
[24 empty] | 1030 | M941C1014 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 150 | 90/160 | 30/60 | 1 | N/A | N/A | 135 ohm | M9484E1017 | Tapped aux shaft | FALSE
[24 empty] | 1031 | M941C1022 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 150 | 90/160 | 30/60 | 1 | N/A | N/A | 135 ohm | M9484E1033 | N/A | FALSE
[24 empty] | 1032 | M941C1030 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 150 | 90/160 | 30/60 | 1 | N/A | N/A | 135 ohm | M9484E1033 | Tapped aux shaft, aux switch set to 7 degrees | FALSE
[24 empty] | 1033 | M941C1048 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 150 | 90/160 | 30/60 | 1 | N/A | N/A | 135 ohm | M9484E1033 | Auxiliary switch set to 4° | FALSE
[24 empty] | 1034 | M941C1055 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 150 | 90/160 | 30/60 | 1 | N/A | N/A | 135 ohm | M9484E1033 | Tapped aux shaft, auxiliary switches set to 4° | FALSE
[24 empty] | 1035 | M941C1063 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 150 | 90/160 | 30/60 | 1 | N/A | N/A | 135 ohm | M9484E1033 | Tapped aux shaft, replaced model includes crank arm | FALSE
[24 empty] | 1036 | M941C1089 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 150 | 90/160 | 30/60 | 1 | N/A | N/A | 135 ohm | NDR | Tapped aux shaft | FALSE
[24 empty] | 1037 | M941C4000 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 150 | 90/160 | 30/60 | 1 | N/A | N/A | 135 ohm | M9484E1017 | Tapped aux shaft, auxiliary switch set to 5 degrees | FALSE
[24 empty] | 1038 | M941C4018 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 150 | 90/160 | 30/60 | 1 | N/A | N/A | 135 ohm | M9484E1017 | Tapped aux shaft, auxiliary switch set to 30 degrees | FALSE
[24 empty] | 1039 | M941D1005 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 150 | 90/160 | 30/60 | 2 | N/A | N/A | 135 ohm | M9484F1007 | Aux switched set to 7/57 degrees | FALSE
[24 empty] | 1040 | M941D1013 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 150 | 90/160 | 30/60 | 2 | N/A | N/A | 135 ohm | M9484F1007 | Tapped aux shaft, auxiliary switch set to 7/57 degrees | FALSE
[24 empty] | 1041 | M941D1021 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 75 | 90/160 | 15/30 | 2 | N/A | N/A | 135 ohm | M9484F1023 | Tapped aux shaft | FALSE
[24 empty] | 1042 | M941D1039 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 150 | 90/160 | 30/60 | 2 | N/A | N/A | 135 ohm | M9484F1031 | Tapped aux shaft, aux switches set to 5/54 degrees | FALSE
[24 empty] | 1043 | M941D1047 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 150 | 90/160 | 30/60 | 2 | N/A | N/A | 135 ohm | M9484F1049 | Tapped aux shaft, aux switches set to 35/120 degrees | FALSE
[24 empty] | 1044 | M941D1054 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 150 | 90/160 | 30/60 | 2 | N/A | N/A | 135 ohm | M9484F1031 | Tapped aux shaft, aux switches set to 5/54 degrees | FALSE
[24 empty] | 1045 | M941D1062 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 150 | 90/160 | 30/60 | 2 | N/A | N/A | 135 ohm | M9484F1031 | Tapped aux shaft, aux switches set to 90/107 degrees | FALSE
[24 empty] | 1046 | M941D1070 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 150 | 90/160 | 30/60 | 2 | N/A | N/A | 135 ohm | M9484F1007 | Tapped aux shaft, aux switches set to 5/54 degrees | FALSE
[24 empty] | 1047 | M941D1112 | N/A | N/A | N/A | N/A | N/A | N/A | 120 | 300 | 90/160 | 60/120 | 2 | N/A | N/A | 135 ohm | NDR | Auxiliary switches to 7/57 degrees | FALSE
[24 empty] | 1048 | M941D4009 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 150 | 90/160 | 30/60 | 2 | N/A | N/A | 135 ohm | M9484F4001 | Tapped aux shaft, auxiliary shaft set to 5/54 degrees | FALSE
[24 empty] | 1049 | M941D4017 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 75 | 90/160 | 15/30 | 2 | N/A | N/A | 135 ohm | M9484F4019 | Tapped aux shaft, auxiliary switches set to 5/54 degrees | FALSE
[24 empty] | 1050 | M941E1012 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 75 | 160 | 30 | N/A | N/A | N/A | 135 ohm | M9484D1010 | N/A | FALSE
[24 empty] | 1051 | M941E1038 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 150 | 160 | 60 | N/A | N/A | N/A | 135 ohm | M9484D1010 | N/A | FALSE
[24 empty] | 1052 | M941E1046 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 150 | 160 | 60 | N/A | N/A | N/A | 135 ohm | M9484D1010 | N/A | FALSE
[24 empty] | 1053 | M941E1053 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 150 | 90 | 60 | N/A | N/A | N/A | 135 ohm | NDR | N/A | FALSE
[24 empty] | 1054 | M941E1061 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 75 | 90 | 60 | N/A | N/A | N/A | 135 ohm | NDR | N/A | FALSE
[24 empty] | 1055 | M943A1004 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 40 | 240 | 90 | 2 | N/A | N/A | 135 ohm | NDR | N/A | FALSE
[24 empty] | 1056 | M944A1002 | M9184D1021 | N/A | N/A | N/A | 160° | N/A | 24 | 150 | 160 | 60 | N/A | N/A | N/A | 135 ohm | M9184A1019 | N/A | FALSE
[24 empty] | 1057 | M944A1010 | M9184D1021 | N/A | N/A | N/A | 160° | N/A | 24 | 150 | 160 | 60 | N/A | N/A | N/A | 135 ohm | M9184A1019 | N/A | FALSE
[24 empty] | 1058 | M944A1028 | M9184D1021 | N/A | N/A | N/A | 90° | N/A | 24 | 150 | 90 | 30 | N/A | N/A | N/A | 135 ohm | M9184A1019 | N/A | FALSE
[24 empty] | 1059 | M944A1036 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 37 | 160 | 15 | N/A | N/A | N/A | 135 ohm | NDR | N/A | FALSE
[24 empty] | 1060 | M944A1044 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 37 | 310 | 15 | N/A | N/A | N/A | 135 ohm | NDR | N/A | FALSE
[24 empty] | 1061 | M944A1051 | M9184D1021 | N/A | N/A | N/A | 90° | N/A | 24 | 75 | 90 | 30 | N/A | N/A | N/A | 135 ohm | M9184F1034 | N/A | FALSE
[24 empty] | 1062 | M944A1069 | M9184D1021 | 50017460-003 | N/A | N/A | 90° | N/A | 120 | 75 | 90 | 30 | N/A | N/A | N/A | 135 ohm | M9184F1034 | N/A | FALSE
[24 empty] | 1063 | M944A1119 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 37 | 335 | 15 | N/A | N/A | N/A | 135 ohm | NDR | N/A | FALSE
[24 empty] | 1064 | M944A1127 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 75 | 335 | 30 | N/A | N/A | N/A | 135 ohm | NDR | N/A | FALSE
[24 empty] | 1065 | M944A1150 | M9184D1021 | N/A | N/A | N/A | 160° | N/A | 24 | 150 | 160 | 120 | N/A | N/A | N/A | 135 ohm | M9194D1003 | N/A | FALSE
[24 empty] | 1066 | M944A1168 | M9184D1021 | N/A | N/A | N/A | 160° | N/A | 24 | 150 | 160 | 60 | N/A | N/A | N/A | 135 ohm | M9184A1019 | N/A | FALSE
[24 empty] | 1067 | M944A1176 | M9184D1021 | N/A | N/A | N/A | 160° | N/A | 24 | 150 | 160 | 60 | N/A | N/A | N/A | 135 ohm | M9184A1019 | N/A | FALSE
[24 empty] | 1068 | M944A1192 | M9184D1021 | N/A | N/A | N/A | 90° | N/A | 24 | 75 | 90 | 30 | N/A | N/A | N/A | 135 ohm | M9184F1034 | N/A | FALSE
[24 empty] | 1069 | M944B1001 | M6284D1000 | N/A | N/A | N/A | 160° | N/A | 24 | 150 | 160 | 60 |  | N/A | N/A | Series 62 | M6284D1000 | No internal balance circuit, requires Q181 when using R927 | FALSE
[24 empty] | 1070 | M944B1019 | M6284D1000 | N/A | N/A | N/A | 160° | N/A | 24 | 150 | 160 | 60 | N/A | N/A | N/A | Series 62 | M6284D1000 | No internal balance circuit, requires Q181 when using R927 | FALSE
[24 empty] | 1071 | M944B1027 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 37 | 160 | 15 | N/A | N/A | N/A | Series 62 | NDR | No internal balance circuit, requires Q181 when using R927 | FALSE
[24 empty] | 1072 | M944B1035 | M6284D1000 | N/A | N/A | N/A | 160° | N/A | 24 | 150 | 160 | 240 | N/A | N/A | N/A | Series 62 | NDR | No internal balance circuit, requires Q181 when using R927 | FALSE
[24 empty] | 1073 | M944B1043 | M6284D1000 | N/A | N/A | N/A | 90° | N/A | 24 | 75 | 90 | 30 | N/A | N/A | N/A | Series 62 | M6284A1055 | No internal balance circuit, requires Q181 when using R927 | FALSE
[24 empty] | 1074 | M944B1167 | M6284D1000 | N/A | N/A | N/A | 160° | N/A | 24 | 150 | 160 | 60 | N/A | N/A | N/A | Series 62 | M6284D1000 | No internal balance circuit, requires Q181 when using R927 | FALSE
[24 empty] | 1075 | M944B1175 | M6284D1000 | N/A | N/A | N/A | 160° | N/A | 24 | 150 | 160 | 60 | N/A | N/A | N/A | Series 62 | M6284D1000 | No internal balance circuit, requires Q181 when using R927 | FALSE
[24 empty] | 1076 | M944B1183 | M6284D1000 | N/A | N/A | N/A | 160° | N/A | 24 | 37 | 160 | 15 | N/A | N/A | N/A | Series 62 | M6284D1000 | No internal balance circuit, check timing and stroke, requires Q181 when using R927 | FALSE
[24 empty] | 1077 | M944B1191 | M6294D1008 | N/A | N/A | N/A | 160° | N/A | 24 | 150 | 160 | 240 | N/A | N/A | N/A | Series 62 | NDR | No internal balance circuit, requires Q181 when using R927 | FALSE
[24 empty] | 1078 | M944B1209 | M6284D1000 | N/A | N/A | N/A | 160° | N/A | 24 | 150 | 160 | 60 | N/A | N/A | N/A | Series 62 | M6284D1000 | No internal balance circuit, requires Q181 when using R927 | FALSE
[24 empty] | 1079 | M944B1241 | M6294D1008 | N/A | 220736A | N/A | 160° | N/A | 24 | 150 | 160 | 240 | 1 | N/A | N/A | Series 62 | NDR | No internal balance circuit, requires Q181 when using R927 | FALSE
[24 empty] | 1080 | M944B4005 | M6284D1000 | N/A | N/A | N/A | ADJ | N/A | 24 | 75 | 90/160 | 15/30 | N/A | N/A | N/A | Series 62 | M6284D1000 | No internal balance circuit, requires Q181 when using R927 | FALSE
[24 empty] | 1081 | M944C1000 | M9184D1021 | N/A | N/A | N/A | ADJ | N/A | 24 | 75 | 90/160 | 15/30 | N/A | N/A | N/A | 135 ohm | M9184D1005 | M9184D is 30/60 second timing | FALSE
[24 empty] | 1082 | M944C1018 | M9194D1003 | N/A | N/A | N/A | ADJ | N/A | 24 | 150 | 90/160 | 120/240 | N/A | N/A | N/A | 135 ohm | M9194D1003 | N/A | FALSE
[24 empty] | 1083 | M944C1042 | M9184D1021 | N/A | N/A | N/A | ADJ | N/A | 24 | 150 | 90/160 | 30/60 | N/A | N/A | N/A | 135 ohm | M9184D1021 | N/A | FALSE
[24 empty] | 1084 | M944C1059 | M9194D1003 | N/A | 220736A | N/A | ADJ | N/A | 24 | 150 | 90/160 | 120/240 | 1 | N/A | N/A | 135 ohm | M9194E1000 | N/A | FALSE
[24 empty] | 1085 | M944C4004 | M9184D1021 | N/A | N/A | N/A | ADJ | N/A | 24 | 150 | 90/160 | 30/60 | N/A | N/A | N/A | 135 ohm | M9184D1021 | N/A | FALSE
[24 empty] | 1086 | M944C4012 | M9184D1021 | N/A | N/A | N/A | ADJ | N/A | 24 | 150 | 90/160 | 120/240 | N/A | N/A | N/A | 135 ohm | M9194D1003 | N/A | FALSE
[24 empty] | 1087 | M944D1009 | M9184D1021 | N/A | 220736B | N/A | ADJ | N/A | 24 | 150 | 90/160 | 30/60 | 2 | N/A | N/A | 135 ohm | M9184F1034 | N/A | FALSE
[24 empty] | 1088 | M944D1017 | M9184D1021 | N/A | 220736B | N/A | ADJ | N/A | 24 | 150 | 90/160 | 30/60 | 2 | N/A | N/A | 135 ohm | M9184F1034 | N/A | FALSE
[24 empty] | 1089 | M944E1008 | M6284D1000 | N/A | 220736B | N/A | ADJ | N/A | 24 | 75 | 90/160 | 15/30 | 2 | N/A | N/A | Series 62 | NDR | M6284 is 30/60 second timing, No internal bal ckt | FALSE
[24 empty] | 1090 | M944E1016 | M6284D1000 | N/A | 220736B | N/A | ADJ | N/A | 24 | 150 | 90/160 | 30/60 | 2 | N/A | N/A | Series 62 | M6284F1013 | No internal balance circuit | FALSE
[24 empty] | 1091 | M944E1024 | M6284D1000 | N/A | 220736B | N/A | ADJ | N/A | 24 | 150 | 90/160 | 30/60 | 2 | N/A | N/A | Series 62 | M6284F1013 | No internal balance circuit, set aux switches at 4 and 54 | FALSE
[24 empty] | 1092 | M944E1032 | M6284D1000 | N/A | 220736B | N/A | ADJ | N/A | 24 | 75 | 90/160 | 15/30 | 2 | N/A | N/A | Series 62 | NDR | Replaced motor is 2X faster, No internal balance circuit | FALSE
[24 empty] | 1093 | M944E1040 | M6284D1000 | N/A | 220736B | N/A | ADJ | N/A | 24 | 150 | 90/160 | 30/60 | 2 | N/A | N/A | Series 62 | M6284F1013 | No internal balance circuit | FALSE
[24 empty] | 1094 | M944E1057 | M6284D1000 | N/A | 220736B | N/A | ADJ | N/A | 24 | 150 | 90/160 | 30/60 | 2 | N/A | N/A | Series 62 | M6284F1013 | No internal balance circuit | FALSE
[24 empty] | 1095 | M944E1081 | M6284D1000 | N/A | 220736B | N/A | 90° | N/A | 24 | 75 | 90 | 30 | 2 | N/A | N/A | Series 62 | M6284F1013 | No internal balance circuit | FALSE
[24 empty] | 1096 | M944E1099 | M6284D1000 | N/A | 220736B | N/A | 90° | N/A | 24 | 150 | 90 | 30 | 2 | N/A | N/A | Series 62 | M6284F1013 | No internal balance circuit | FALSE
[24 empty] | 1097 | M944F1007 | M9184D1021 | N/A | N/A | N/A | 160° | N/A | 24 | 150 | 160 | 60 | N/A | N/A | N/A | 135 ohm | M9184A1019 | Use Q181 for slaved motor applications | FALSE
[24 empty] | 1098 | M944G1006 | M9184D1021 | N/A | 220736B | N/A | 160° | N/A | 24 | 150 | 160 | 60 | 2 | N/A | N/A | Series 62 | M9184F1034 | N/A | FALSE
[24 empty] | 1099 | M944G1014 | M9184D1021 | N/A | 220736B | N/A | 160° | N/A | 24 | 150 | 160 | 60 | 2 | N/A | N/A | Series 62 | M9184F1034 | N/A | FALSE
[24 empty] | 1100 | M944G1022 | M6284D1000 | 50017460-003 | N/A | N/A | 160° | N/A | 120 | 150 | 160 | 60 | N/A | N/A | N/A | Series 62 | m6284a1055 | No internal balance circuit, change control circuit to 24 Vac | FALSE
[24 empty] | 1101 | M944G1030 | M6284D1000 | 50017460-003 | N/A | N/A | 90° | N/A | 120 | 150 | 90 | 30 | N/A | N/A | N/A | Series 62 | M6284A1055 | No internal balance circuit, change control circuit to 24 Vac | FALSE
[24 empty] | 1102 | M944G1048 | M6284D1000 | 50017460-003 | N/A | N/A | 160° | N/A | 120 | 150 | 160 | 60 | N/A | N/A | N/A | Series 62 | m6284a1055 | No internal balance circuit, change control circuit to 24 Vac | FALSE
[24 empty] | 1103 | M944G1055 | M6284D1000 | 50017460-003 | N/A | N/A | 160° | N/A | 120 | 150 | 160 | 240 | N/A | N/A | N/A | Series 62 | NDR | No internal balance circuit | FALSE
[24 empty] | 1104 | M944G1063 | M6284D1000 | 50017460-003 | N/A | N/A | 160° | N/A | 120 | 150 | 160 | 60 | N/A | N/A | N/A | Series 62 | m6284a1055 | No internal balance circuit, change control circuit to 24 Vac | FALSE
[24 empty] | 1105 | M944G1071 | M6284D1000 | 50017460-003 | N/A | N/A | 90° | N/A | 120 | 150 | 90 | 30 | N/A | N/A | N/A | Series 62 | M6284A1055 | No internal balance circuit, change control circuit to 24 Vac | FALSE
[24 empty] | 1106 | M944G1089 | M6284D1000 | 50017460-003 | N/A | N/A | 160° | N/A | 120 | 150 | 160 | 60 | N/A | N/A | N/A | Series 62 | m6284a1055 | No internal balance circuit, change control circuit to 24 Vac | FALSE
[24 empty] | 1107 | M944G1097 | M6284D1000 | 50017460-003 | N/A | N/A | 90° | N/A | 120 | 150 | 90 | 30 | N/A | N/A | N/A | Series 62 | M6284A1055 | No internal balance circuit, change control circuit to 24 Vac | FALSE
[24 empty] | 1108 | M944G1105 | M6294D1008 | 50017460-003 | N/A | N/A | 160° | N/A | 120 | 150 | 160 | 240 | N/A | N/A | N/A | Series 62 | NDR | No internal balance circuit | FALSE
[24 empty] | 1109 | M944G1121 | M6294D1008 | 50017460-003 | 220736A | N/A | 160° | N/A | 120 | 150 | 160 | 240 | 1 | N/A | N/A | Series 62 | NDR | No internal balance circuit | FALSE
[24 empty] | 1110 | M944H1013 | M6284D1000 | 50017460-003 | 220736A | N/A | 160° | N/A | 120 | 150 | 160 | 60 | 1 | N/A | N/A | Series 62 | M6284F1013 | No internal balance circuit, change control circuit to 24 Vac | FALSE
[24 empty] | 1111 | M944H1021 | M6284D1000 | 50017460-003 | 220736A | N/A | 160° | N/A | 120 | 150 | 160 | 60 | 1 | N/A | N/A | Series 62 | M6284F1013 | No internal balance circuit, change control circuit to 24 Vac | FALSE
[24 empty] | 1112 | M944H1039 | M6284D1000 | 50017460-003 | 220736A | N/A | 160° | N/A | 120 | 150 | 160 | 60 | 1 | N/A | N/A | Series 62 | M6284F1013 | No internal balance circuit, change control circuit to 24 Vac | FALSE
[24 empty] | 1113 | M944H1047 | M6284D1000 | 50017460-003 | 220736A | N/A | 160° | N/A | 120 | 150 | 160 | 60 | 1 | N/A | N/A | Series 62 | M6284F1013 | No internal balance circuit | FALSE
[24 empty] | 1114 | M944H1062 | M6294D1008 | 50017460-003 | 220736A | N/A | 160° | N/A | 120 | 150 | 160 | 240 | 1 | N/A | N/A | Series 62 | NDR | Trane Special, No internal balance circuit | FALSE
[24 empty] | 1115 | M944J1002 | M6284D1000 | N/A | N/A | N/A | 160° | N/A | 24 | 150 | 160 | 60 | N/A | N/A | N/A | Series 62 | M6284D1000 | Requires Q181 for auxiliary pot, and when using R927 | FALSE
[24 empty] | 1116 | M944J1051 | M6284D1000 | N/A | N/A | N/A | 160° | N/A | 24 | 150 | 160 | 60 | N/A | N/A | N/A | Series 62 | M6284D1000 | Requires Q181 for aux pot, and when using R927 | FALSE
[24 empty] | 1117 | M944K1001 | M6284D1000 | 50017460-003 | 220736B | N/A | 160° | N/A | 120 | 150 | 160 | 60 | 2 | N/A | N/A | Series 62 | M6284F1013 | No internal balance circuit, change control circuit to 24 Vac | FALSE
[24 empty] | 1118 | M944K1019 | M6284D1000 | 50017460-003 | 220736B | N/A | 160° | N/A | 120 | 150 | 160 | 60 | 2 | N/A | N/A | Series 62 | M6284F1013 | No internal balance circuit, change control circuit to 24 Vac | FALSE
[24 empty] | 1119 | M944L1018 | M9184D1021 | 50017460-003 | N/A | N/A | ADJ | N/A | 120 | 150 | 90/160 | 120/240 | N/A | N/A | N/A | 135 ohm | NDR | N/A | FALSE
[24 empty] | 1120 | M944N1024 | M9184D1021 | N/A | 220736A | N/A | 160° | N/A | 24 | 75 | 160 | 30 | 1 | N/A | N/A | 135 ohm | M6184D1001 | N/A | FALSE
[24 empty] | 1121 | M944N1032 | M9184D1021 | N/A | 220736A | N/A | 90° | N/A | 24 | 150 | 90 | 30 | 1 | N/A | N/A | 135 ohm | M9184F1034 | N/A | FALSE
[24 empty] | 1122 | M944N1040 | M9184D1021 | N/A | 220736A | N/A | 90° | N/A | 24 | 150 | 90 | 30 | 1 | N/A | N/A | 135 ohm | M9184F1034 | N/A | FALSE
[24 empty] | 1123 | M944N1057 | M9184D1021 | N/A | 220736A | N/A | 160° | N/A | 24 | 150 | 160 | 60 | 1 | N/A | N/A | 135 ohm | M9184F1034 | N/A | FALSE
[24 empty] | 1124 | M944N1065 | M9184D1021 | N/A | 220736A | N/A | 160° | N/A | 24 | 75 | 160 | 30 | 1 | N/A | N/A | 135 ohm | M6184D1001 | M9184D is 60 sec at 160° stroke | FALSE
[24 empty] | 1125 | M944N1073 | M9184D1021 | N/A | 220736A | N/A | 90° | N/A | 24 | 150 | 90 | 30 | 1 | N/A | N/A | 135 ohm | M9184F1034 | N/A | FALSE
[24 empty] | 1126 | M944N1081 | M9184D1021 | N/A | 220736A | N/A | 90° | N/A | 24 | 150 | 90 | 30 | 1 | N/A | N/A | 135 ohm | M9184F1034 | N/A | FALSE
[24 empty] | 1127 | M944P1014 | M9184D1021 | N/A | 220736B | N/A | 90° | N/A | 24 | 150 | 90 | 30 | 2 | N/A | N/A | 135 ohm | M9184F1034 | N/A | FALSE
[24 empty] | 1128 | M944P1022 | M9184D1021 | N/A | 220736B | N/A | 90° | N/A | 24 | 150 | 90 | 30 | 2 | N/A | N/A | 135 ohm | M9184F1034 | N/A | FALSE
[24 empty] | 1129 | M944P1030 | M9184D1021 | N/A | 220736B | N/A | 90° | N/A | 24 | 150 | 90 | 30 | 2 | N/A | N/A | 135 ohm | M9184F1034 | N/A | FALSE
[24 empty] | 1130 | M944P1048 | M9184D1021 | N/A | 220736B | N/A | 90° | N/A | 24 | 150 | 90 | 30 | 2 | N/A | N/A | 135 ohm | M9184F1034 | N/A | FALSE
[24 empty] | 1131 | M944R1012 | M6294D1008 | 50017460-003 | 220736A | N/A | 160° | N/A | 120 | 150 | 160 | 120 | 1 | N/A | N/A | Series 62 | NDR | Check timing and stroke, requires Q181 when using R927 | FALSE
[24 empty] | 1132 | M944R1020 | M6294D1008 | 50017460-003 | 220736B | N/A | 160° | N/A | 120 | 150 | 160 | 120 | 2 | N/A | N/A | Series 62 | NDR | Check timing and stroke, requires Q181 when using R927 | FALSE
[24 empty] | 1133 | M944S1001 | M6284D1000 | 50017460-003 | 220736B | N/A | ADJ | N/A | 120 | 75 | 90/160 | 15/30 | 2 | N/A | N/A | Series 62 | NDR | M6284 is 30/60 second timing, No internal balancing ckt | FALSE
[24 empty] | 1134 | M944S1019 | M6284D1000 | 50017460-003 | 220736B | N/A | ADJ | N/A | 120 | 150 | 90/160 | 30/60 | 2 | N/A | N/A | Series 62 | M6284F1013 | No internal balance circuit | FALSE
[24 empty] | 1135 | M944S1027 | M6284D1000 | 50017460-003 | 220736B | N/A | ADJ | N/A | 120 | 150 | 90/160 | 30/60 | 2 | N/A | N/A | Series 62 | M6284F1013 | No internal balance circuit | FALSE
[24 empty] | 1136 | M945A1009 | M9185D1004 | N/A | N/A | N/A | 160° | N/A | 24 | 50 | 160 | 60 | N/A | N/A | N/A | 135 ohm | M9185A1018 | N/A | FALSE
[24 empty] | 1137 | M945A1017 | M9185D1004 | N/A | N/A | N/A | 160° | N/A | 24 | 50 | 160 | 60 | N/A | N/A | N/A | 135 ohm | M9185A1018 | N/A | FALSE
[24 empty] | 1138 | M945A1025 | M9185D1004 | N/A | N/A | N/A | 160° | N/A | 24 | 50 | 160 | 60 | N/A | N/A | N/A | 135 ohm | M9185A1018 | N/A | FALSE
[24 empty] | 1139 | M945A1033 | M9185D1004 | N/A | N/A | N/A | 160° | N/A | 24 | 50 | 160 | 60 | N/A | N/A | N/A | 135 ohm | M9185A1018 | N/A | FALSE
[24 empty] | 1140 | M945A1066 | M9185D1004 | N/A | N/A | N/A | 160° | N/A | 24 | 50 | 160 | 60 | N/A | N/A | N/A | 135 ohm | M9185A1018 | N/A | FALSE
[24 empty] | 1141 | M945A1074 | M9185D1004 | N/A | N/A | N/A | 90° | N/A | 24 | 50 | 90 | 35 | N/A | N/A | N/A | 135 ohm | M9185A1018 | N/A | FALSE
[24 empty] | 1142 | M945A1082 | M9185D1004 | N/A | N/A | N/A | 90° | N/A | 24 | 50 | 90 | 35 | N/A | N/A | N/A | 135 ohm | M9185A1018 | N/A | FALSE
[24 empty] | 1143 | M945A1090 | M9185D1004 | N/A | N/A | N/A | 160° | N/A | 24 | 50 | 160 | 60 | N/A | N/A | N/A | 135 ohm | M9185D1004 | N/A | FALSE
[24 empty] | 1144 | M945A1108 | M9185D1004 | N/A | N/A | N/A | 160° | N/A | 24 | 50 | 160 | 60 | N/A | N/A | N/A | 135 ohm | M9185A1018 | N/A | FALSE
[24 empty] | 1145 | M945A1116 | M9185D1004 | N/A | N/A | N/A | 90° | N/A | 24 | 50 | 90 | 35 | N/A | N/A | N/A | 135 ohm | M9185A1018 | N/A | FALSE
[24 empty] | 1146 | M945A1124 | M9185D1004 | N/A | N/A | N/A | 90° | N/A | 24 | 50 | 90 | 35 | N/A | N/A | N/A | 135 ohm | M9185A1018 | N/A | FALSE
[24 empty] | 1147 | M945A1157 | M9185D1004 | N/A | N/A | N/A | ADJ | N/A | 24 | 50 | 90/160 | 30/60 | N/A | N/A | N/A | 135 ohm | M9185D1004 | N/A | FALSE
[24 empty] | 1148 | M945A4003 | M9185D1004 | N/A | N/A | N/A | ADJ | N/A | 24 | 50 | 90/160 | 30/60 | N/A | N/A | N/A | 135 ohm | M9185D1004 | N/A | FALSE
[24 empty] | 1149 | M945AA1007 | M9185D1004 | N/A | 220736B | N/A | 90° | N/A | 24 | 50 | 90 | 60 | 2 | N/A | N/A | N/A | NDR | M9185D is 30 seconds, 90° stroke, use auxilliary end | FALSE
[24 empty] | 1150 | M945AB1005 | M9185D1004 | N/A | 220736A | N/A | 90° | N/A | 24 | 50 | 90 | 60 | 1 | N/A | N/A | N/A | NDR | M9185 is 30 sec at 90° stroke | FALSE
[24 empty] | 1151 | M945AB1013 | M9185D1004 | N/A | 220736A | N/A | 90° | N/A | 24 | 50 | 90 | 60 | 1 | N/A | N/A | N/A | NDR | M9185 is 30 sec at 90° stroke | FALSE
[24 empty] | 1152 | M945AD1001 | M6284A1005 | N/A | N/A | N/A | 90° | N/A | 24 | 25 | 90 | 60 | N/A | N/A | N/A | Series 62 | NDR | Trane Special, No internal balance circuit | FALSE
[24 empty] | 1153 | M945B1057 | M6285A1005 | N/A | N/A | N/A | 160° | N/A | 24 | 50 | 160 | 60 | N/A | N/A | N/A | Series 62 | M6285A1005 | No internal balance circuit | FALSE
[24 empty] | 1154 | M945B1065 | M6284A1005 | N/A | N/A | N/A | 90° | N/A | 24 | 50 | 90 | 30 | N/A | N/A | N/A | Series 62 | M6284A1005 | No internal balance circuit | FALSE
[24 empty] | 1155 | M945B1073 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 50 | 90 | 30 | N/A | N/A | N/A | Series 62 | NDR | N/A | FALSE
[24 empty] | 1156 | M945B1081 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 50 | 160 | 60 | N/A | N/A | N/A | Series 62 | NDR | N/A | FALSE
[24 empty] | 1157 | M945B1115 | M6284A1005 | 50017460-003 | N/A | N/A | 90° | N/A | 120 | 50 | 90 | 30 | N/A | N/A | N/A | Series 62 | NDR | No internal balance circuit | FALSE
[24 empty] | 1158 | M945B4002 | M6285A1005 | N/A | N/A | N/A | 160° | N/A | 24 | 50 | 160 | 60 | N/A | N/A | N/A | Series 62 | M6285A1005 | No internal balance circuit | FALSE
[24 empty] | 1159 | M945C1007 | M6285A1005 | N/A | 220736B | N/A | 160° | N/A | 24 | 50 | 160 | 60 | 2 | N/A | N/A | Series 62 | M6285C1001 | No internal balance circuit | FALSE
[24 empty] | 1160 | M945C1015 | M6285A1005 | N/A | 220736B | N/A | 160° | N/A | 24 | 50 | 160 | 60 | 2 | N/A | N/A | Series 62 | M6285C1001 | No internal balance circuit | FALSE
[24 empty] | 1161 | M945C1031 | M6284A1005 | N/A | 220736A | N/A | 90° | N/A | 24 | 50 | 90 | 30 | 1 | N/A | N/A | Series 62 | NDR | No internal balance circuit | FALSE
[24 empty] | 1162 | M945D1006 | M9185D1004 | N/A | 220736B | N/A | 160° | N/A | 24 | 50 | 160 | 60 | 2 | N/A | N/A | 135 ohm | M9185C1006 | N/A | FALSE
[24 empty] | 1163 | M945D1030 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 50 | 160 | 60 | 2 | N/A | N/A | 135 ohm | NDR | UL555 refer to damper mfr. | FALSE
[24 empty] | 1164 | M945D1048 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 50 | 160 | 60 | 2 | N/A | N/A | 135 ohm | NDR | UL555 refer to damper mfr. | FALSE
[24 empty] | 1165 | M945E1005 | M9185D1004 | N/A | N/A | Q181A1007 | 160° | N/A | 24 | 50 | 160 | 60 | N/A | N/A | N/A | 135 ohm | M9185A1018 | Q181: slaved motor application | FALSE
[24 empty] | 1166 | M945E1013 | M9185D1004 | N/A | N/A | Q181A1007 | 160° | N/A | 24 | 50 | 160 | 60 | N/A | N/A | N/A | 135 ohm | M9185A1018 | Q181: slaved motor application | FALSE
[24 empty] | 1167 | M945F1004 | M9185D1004 | N/A | N/A | N/A | 160° | N/A | 24 | 50 | 160 | 60 | N/A | N/A | N/A | 135 ohm | M9185A1018 | Use auxiliary end of motor | FALSE
[24 empty] | 1168 | M945F1038 | M9185D1004 | N/A | N/A | N/A | 160° | N/A | 24 | 50 | 160 | 60 | N/A | N/A | N/A | 135 ohm | M9185A1018 | Use auxiliary end of motor | FALSE
[24 empty] | 1169 | M945F1046 | M9185D1004 | 50017460-001 | N/A | N/A | 160° | N/A | 208 | 50 | 160 | 60 | N/A | N/A | N/A | 135 ohm | NDR | Use auxiliary end of motor | FALSE
[24 empty] | 1170 | M945F1053 | M9185D1004 | N/A | N/A | N/A | 160° | N/A | 24 | 50 | 160 | 60 | N/A | N/A | N/A | 135 ohm | M9185A1018 | Use auxiliary end of motor | FALSE
[24 empty] | 1171 | M945F4008 | M9185D1004 | N/A | N/A | N/A | 160° | N/A | 24 | 50 | 160 | 60 | N/A | N/A | N/A | 135 ohm | M9185A1018 | Use auxiliary end of motor | FALSE
[24 empty] | 1172 | M945G1003 | M6285A1005 | N/A | N/A | N/A | 160° | N/A | 24 | 50 | 160 | 60 | N/A | N/A | N/A | Series 62 | M6285A1005 | Use auxiliary end of motor | FALSE
[24 empty] | 1173 | M945G1037 | M6285A1005 | N/A | N/A | N/A | 160° | N/A | 24 | 50 | 160 | 60 | N/A | N/A | N/A | Series 62 | M6285A1005 | Use auxiliary end of motor | FALSE
[24 empty] | 1174 | M945G1045 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 50 | 160 | 60 | N/A | N/A | N/A | Series 62 | NDR | N/A | FALSE
[24 empty] | 1175 | M945G1052 | N/A | N/A | N/A | N/A | N/A | N/A | 220 | 50 | 160 | 60 | N/A | N/A | N/A | Series 62 | NDR | N/A | FALSE
[24 empty] | 1176 | M945H1002 | M9185D1004 | N/A | 220736B | N/A | 160° | N/A | 24 | 50 | 160 | 60 | 2 | N/A | N/A | 135 ohm | M9185C1006 | N/A | FALSE
[24 empty] | 1177 | M945H1010 | M9185D1004 | N/A | 220736B | N/A | 160° | N/A | 24 | 50 | 160 | 60 | 2 | N/A | N/A | 135 ohm | M9185C1006 | N/A | FALSE
[24 empty] | 1178 | M945J1009 | M9185D1004 | N/A | 220736A | N/A | 160° | N/A | 24 | 50 | 160 | 60 | 1 | N/A | N/A | 135 ohm | M9185C1006 | N/A | FALSE
[24 empty] | 1179 | M945J1017 | M9185D1004 | N/A | 220736A | N/A | 160° | N/A | 24 | 50 | 160 | 60 | 1 | N/A | N/A | 135 ohm | M9185C1006 | N/A | FALSE
[24 empty] | 1180 | M945J1025 | M9185D1004 | N/A | 220736B | N/A | 160° | N/A | 24 | 50 | 160 | 60 | 2 | N/A | N/A | 135 ohm | M9185C1006 | N/A | FALSE
[24 empty] | 1181 | M945J1033 | M9185D1004 | 50017460-003 | 220736B | N/A | 160° | N/A | 120 | 50 | 160 | 60 | 2 | N/A | N/A | 135 ohm | NDR | N/A | FALSE
[24 empty] | 1182 | M945K1008 | M6285A1005 | N/A | 220736B | N/A | 160° | N/A | 24 | 50 | 160 | 60 | 2 | N/A | N/A | Series 62 | M6285C1001 | No internal balance circuit | FALSE
[24 empty] | 1183 | M945K1016 | M6285A1005 | N/A | 220736B | N/A | 160° | N/A | 24 | 50 | 160 | 60 | 2 | N/A | N/A | Series 62 | M6285C1001 | No internal balance circuit | FALSE
[24 empty] | 1184 | M945L1007 | M6285A1005 | N/A | N/A | N/A | 160° | N/A | 24 | 50 | 160 | 60 | N/A | N/A | N/A | Series 62 | M6285A1005 | Requires Q181 when using R927 | FALSE
[24 empty] | 1185 | M945L1015 | M6285A1005 | N/A | N/A | N/A | 160° | N/A | 24 | 50 | 160 | 60 | N/A | N/A | N/A | Series 62 | M6285A1005 | Requires Q181 when using R927 | FALSE
[24 empty] | 1186 | M945M1006 | M9185D1004 | N/A | N/A | N/A | 160° | N/A | 24 | 50 | 160 | 60 | N/A | N/A | N/A | 135 ohm | M9185A1018 | N/A | FALSE
[24 empty] | 1187 | M945M1022 | M9185D1004 | 50017460-001 | N/A | N/A | 160° | N/A | 208/240 | 50 | 160 | 60 | N/A | N/A | N/A | 135 ohm | NDR | N/A | FALSE
[24 empty] | 1188 | M945M1030 | M9185D1004 | N/A | N/A | N/A | 160° | N/A | 24 | 50 | 160 | 60 | N/A | N/A | N/A | 135 ohm | M9185A1018 | N/A | FALSE
[24 empty] | 1189 | M945M1048 | M9185D1004 | N/A | N/A | N/A | 160° | N/A | 24 | 50 | 160 | 60 | N/A | N/A | N/A | 135 ohm | M9185A1018 | N/A | FALSE
[24 empty] | 1190 | M945Y1002 | M6285A1005 | N/A | N/A | Q181A1007 | 160° | N/A | 24 | 50 | 160 | 60 | N/A | N/A | N/A | Series 62 | M6285A1005 | Q181: slaved motor application | FALSE
[24 empty] | 1191 | M945Y1010 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 50 | 90 | 60 |  | N/A | N/A | 135 ohm | NDR | N/A | FALSE
[24 empty] | 1192 | M945Z1001 | M9185D1004 | N/A | 220736B | N/A | 160° | N/A | 24 | 50 | 160 | 60 | 2 | N/A | N/A | 135 ohm | M9185A1018 | N/A | FALSE
[24 empty] | 1193 | M945Z1019 | M9185D1004 | 50017460-001 | N/A | N/A | 160° | N/A | 208 /240 | 50 | 160 | 60 | N/A | N/A | N/A | 135 ohm | NDR | N/A | FALSE
[24 empty] | 1194 | M9481D1005 | M9484F1007 | N/A | N/A | N/A | N/A | N/A | 24 | 150 | 90/160 | 30/60 | N/A | 1 | N/A | 135 ohm | M9484D1010 | N/A | FALSE
[24 empty] | 1195 | M9481E1002 | M9484F1007 | N/A | N/A | N/A | N/A | N/A | 24 | 150 | 90/160 | 30/60 | 1 | 1 | N/A | 135 ohm | M9484E1017 | N/A | TRUE
[24 empty] | 1196 | M9481F1000 | M9484F1007 | N/A | N/A | N/A | N/A | 7 & 80 | 24 | 150 | 90/160 | 30/60 | 2 | 1 | N/A | 135 ohm | M9484F1007 | N/A | TRUE
[24 empty] | 1197 | M9484D1002 | M9484D1010 | N/A | N/A | N/A | N/A | N/A | 24 | 75 | 90/160 | 15/30 | N/A | 2 | N/A | 135 ohm | M9484D1010 | N/A | TRUE
[24 empty] | 1198 | M9484D1010 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 150 | 90/160 | 30/60 | N/A | 2 | N/A | 135 ohm | N/A | With tapped shaft | TRUE
[24 empty] | 1199 | M9484D1028 | NDR | N/A | N/A | N/A | N/A | N/A | 24 | 150 | 90/160 | 30/60 | N/A | 2 | YES | 135 ohm | M9484D1010 | With tapped shaft | TRUE
[24 empty] | 1200 | M9484D1036 | NDR | N/A | N/A | N/A | N/A | N/A | 24 | 75 | 90/160 | 15/30 | N/A | 2 | YES | 135 ohm | M9484D1010 | N/A | TRUE
[24 empty] | 1201 | M9484D1044 | NDR | N/A | N/A | N/A | N/A | N/A | 24 | 150 | 90/160 | 30/60 | N/A | 2 | N/A | 135 ohm | M9484D1010 | With tapped shaft | TRUE
[24 empty] | 1202 | M9484D1051 | NDR | N/A | N/A | N/A | N/A | N/A | 24 | 150 | 90/160 | 30/60 | N/A | 2 | N/A | 135 ohm | M9484D1010 | With tapped shaft | TRUE
[24 empty] | 1203 | M9484D4006 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 150 | 90/160 | 30/60 | N/A | 2 | YES | 135 ohm | N/A | Canada, tapped shaft, 220741A | TRUE
[24 empty] | 1204 | M9484E1009 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 75 | 90/160 | 15/30 | 1 | 2 | N/A | 135 ohm | N/A | With tapped shaft | TRUE
[24 empty] | 1205 | M9484E1017 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 150 | 90/160 | 30/60 | 1 | 2 | N/A | 135 ohm | N/A | With tapped shaft | TRUE
[24 empty] | 1206 | M9484E1025 | NDR | N/A | N/A | N/A | N/A | N/A | 24 | 150 | 90/160 | 30/60 | 1 | 2 | YES | 135 ohm | M9484E1033 | N/A | TRUE
[24 empty] | 1207 | M9484E1033 | N/A | N/A | N/A | N/A | N/A | 7 | 24 | 150 | 90/160 | 30/60 | 1 | 2 | N/A | 135 ohm | N/A | N/A | TRUE
[24 empty] | 1208 | M9484E1041 | NDR | N/A | N/A | N/A | N/A | 7 | 24 | 150 | 90/160 | 30/60 | 1 | 2 | N/A | 135 ohm | M9484E1033 | With 221455A | TRUE
[24 empty] | 1209 | M9484E1058 | NDR | N/A | N/A | N/A | N/A | 7 | 24 | 150 | 90/160 | 30/60 | 1 | 2 | N/A | 135 ohm | M9484E1033 | N/A | TRUE
[24 empty] | 1210 | M9484E1066 | NDR | N/A | N/A | N/A | N/A | N/A | 24 | 150 | 90/160 | 30/60 | 1 | 2 | N/A | 135 ohm | M9484E1033 | N/A | TRUE
[24 empty] | 1211 | M9484E1074 | NDR | N/A | N/A | N/A | N/A | 7 | 24 | 150 | 90/160 | 30/60 | 1 | 2 | N/A | 135 ohm | M9484E1033 | N/A | TRUE
[24 empty] | 1212 | M9484E1082 | NDR | N/A | N/A | N/A | N/A | 7 | 24 | 150 | 90/160 | 30/60 | 1 | 2 | N/A | 135 ohm | M9484E1033 | With tapped shaft | TRUE
[24 empty] | 1213 | M9484E1090 | NDR | N/A | N/A | N/A | N/A | N/A | 24 | 150 | 90/160 | 30/60 | 1 | 2 | N/A | 135 ohm | M9484E1017 | With tapped shaft | TRUE
[24 empty] | 1214 | M9484E1116 | NDR | N/A | N/A | N/A | N/A | N/A | 24 | 75 | 90/160 | 15/30 | 1 | 2 | N/A | 135 ohm | M9484E1009 | With tapped shaft | TRUE
[24 empty] | 1215 | M9484E4003 | N/A | N/A | N/A | N/A | N/A | 5 | 24 | 150 | 90/160 | 30/60 | 1 | 2 | YES | 135 ohm | N/A | Canada, tapped shaft, 220741A | TRUE
[24 empty] | 1216 | M9484F1007 | N/A | N/A | N/A | N/A | N/A | 7 & 80 | 24 | 150 | 90/160 | 30/60 | 2 | 2 | N/A | 135 ohm | N/A | N/A | TRUE
[24 empty] | 1217 | M9484F1015 | NDR | N/A | N/A | N/A | N/A | 7 & 80 | 24 | 150 | 90/160 | 30/60 | 2 | 2 | N/A | 135 ohm | M9484F1007 | N/A | TRUE
[24 empty] | 1218 | M9484F1023 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 75 | 90/160 | 15/30 | 2 | 2 | N/A | 135 ohm | N/A | With tapped shaft | TRUE
[24 empty] | 1219 | M9484F1031 | N/A | N/A | N/A | N/A | N/A | 7 & 80 | 24 | 150 | 90/160 | 30/60 | 2 | 2 | N/A | 135 ohm | N/A | With tapped shaft | TRUE
[24 empty] | 1220 | M9484F1049 | N/A | N/A | N/A | N/A | N/A | 35 & 120 | 24 | 150 | 90/160 | 30/60 | 2 | 2 | N/A | 135 ohm | N/A | N/A | TRUE
[24 empty] | 1221 | M9484F1056 | NDR | N/A | N/A | N/A | N/A | N/A | 24 | 75 | 90/160 | 15/30 | 2 | 2 | N/A | 135 ohm | M9484F1023 | With tapped shaft | TRUE
[24 empty] | 1222 | M9484F1064 | NDR | N/A | N/A | N/A | N/A | 7 & 80 | 24 | 150 | 90/160 | 30/60 | 2 | 2 | N/A | 135 ohm | M9484F1031 | With tapped shaft | TRUE
[24 empty] | 1223 | M9484F1072 | NDR | N/A | N/A | N/A | N/A | 7 & 80 | 24 | 150 | 90/160 | 30/60 | 2 | 2 | N/A | 135 ohm | M9484F1007 | N/A | TRUE
[24 empty] | 1224 | M9484F4001 | N/A | N/A | N/A | N/A | N/A | 54 & 5 | 24 | 150 | 90/160 | 30/60 | 2 | 2 | YES | 135 ohm | N/A | Canada, tapped shaft, 220741A | TRUE
[24 empty] | 1225 | M9484F4019 | N/A | N/A | N/A | N/A | N/A | 54 & 5 | 24 | 75 | 90/160 | 15/30 | 2 | 2 | YES | 135 ohm | N/A | Canada, tapped shaft, 220741A | TRUE
[24 empty] | 1226 | M9491D1003 | NDR | N/A | N/A | N/A | N/A | N/A | 24 | 300 | 90/160 | 60/120 | N/A | 1 | N/A | 135 ohm | M9494D1000 | N/A | TRUE
[24 empty] | 1227 | M9494D1000 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 300 | 90/160 | 60/120 | N/A | 2 | N/A | 135 ohm | N/A | N/A | TRUE
[24 empty] | 1228 | M954A1001 | M9184D1021 | N/A | N/A | N/A | ADJ | N/A | 24 | 150 | 90/160 | 30/60 | N/A | N/A | N/A | 135 ohm | M9184D1021 | N/A | TRUE
[24 empty] | 1229 | M954A1019 | M9184D1021 | N/A | N/A | N/A | ADJ | N/A | 24 | 150 | 90/160 | 30/60 | N/A | N/A | N/A | 135 ohm | M9184D1021 | N/A | FALSE
[24 empty] | 1230 | M954A1027 | M9184D1021 | N/A | N/A | N/A | ADJ | N/A | 24 | 150 | 90/160 | 30/60 | N/A | N/A | N/A | 135 ohm | M9184D1021 | N/A | FALSE
[24 empty] | 1231 | M954A1035 | M9184D1021 | N/A | N/A | N/A | ADJ | N/A | 24 | 150 | 90/160 | 30/60 | N/A | N/A | N/A | 135 ohm | M9184D1021 | N/A | FALSE
[24 empty] | 1232 | M954B1000 | M9184D1021 | N/A | 220736B | N/A | 160° | N/A | 24 | 150 | 160 | 60 | 2 | N/A | N/A | 135 ohm | M9184F1034 | N/A | FALSE
[24 empty] | 1233 | M954B1018 | M9184D1021 | N/A | 220736B | N/A | 90° | N/A | 24 | 150 | 90 | 30 | 2 | N/A | N/A | 135 ohm | M9184C1031 | N/A | FALSE
[24 empty] | 1234 | M954B1026 | M9184D1021 | N/A | 220736B | N/A | 90° | N/A | 24 | 150 | 90 | 30 | 2 | N/A | N/A | 135 ohm | M9184C1031 | N/A | FALSE
[24 empty] | 1235 | M954B1034 | M9184D1021 | N/A | 220736B | N/A | 90° | N/A | 24 | 150 | 90 | 30 | 2 | N/A | N/A | 135 ohm | M9184C1031 | N/A | FALSE
[24 empty] | 1236 | M954B1042 | M9184D1021 | N/A | 220736B | N/A | 90° | N/A | 24 | 150 | 90 | 30 | 2 | N/A | N/A | 135 ohm | M9184C1031 | N/A | FALSE
[24 empty] | 1237 | M954B1059 | M9184D1021 | 50017460-003 | 220736B | N/A | 160° | N/A | 120 | 75 | 160 | 30 | 2 | N/A | N/A | 135 ohm | M9184D1005 | N/A | FALSE
[24 empty] | 1238 | M954B1067 | M9184D1021 | N/A | 220736B | N/A | 160° | N/A | 24 | 150 | 160 | 60 | 2 | N/A | N/A | 135 ohm | M9184F1034 | N/A | FALSE
[24 empty] | 1239 | M954B1075 | M9184D1021 | N/A | 220736B | N/A | 90° | N/A | 24 | 150 | 90 | 30 | 2 | N/A | N/A | 135 ohm | NDR | Cleaver Brooks Special | FALSE
[24 empty] | 1240 | M954C1009 | M9184D1021 | N/A | 220736A | N/A | 160° | N/A | 24 | 75 | 160 | 30 | 1 | N/A | N/A | 135 ohm | M9184D1005 | N/A | FALSE
[24 empty] | 1241 | M954C1017 | M9184D1021 | N/A | 220736A | N/A | 90° | N/A | 24 | 150 | 90 | 30 | 1 | N/A | N/A | 135 ohm | M9184F1034 | N/A | FALSE
[24 empty] | 1242 | M954C1025 | M9184D1021 | N/A | 220736A | N/A | 90° | N/A | 24 | 150 | 90 | 30 | 1 | N/A | N/A | 135 ohm | M9184F1034 | N/A | FALSE
[24 empty] | 1243 | M954C1033 | M9184D1021 | N/A | 220736A | N/A | 160° | N/A | 24 | 150 | 160 | 60 | 1 | N/A | N/A | 135 ohm | M9184F1034 | N/A | FALSE
[24 empty] | 1244 | M954C1041 | M9184D1021 | N/A | 220736A | N/A | 160° | N/A | 24 | 75 | 160 | 30 | 1 | N/A | N/A | 135 ohm | M9184D1005 | N/A | FALSE
[24 empty] | 1245 | M954C1058 | M9184D1021 | N/A | 220736A | N/A | 90° | N/A | 24 | 150 | 90 | 30 | 1 | N/A | N/A | 135 ohm | M9184F1034 | N/A | FALSE
[24 empty] | 1246 | M954C1066 | M9184D1021 | N/A | 220736A | N/A | 90° | N/A | 24 | 150 | 90 | 30 | 1 | N/A | N/A | 135 ohm | M9184F1034 | N/A | FALSE
[24 empty] | 1247 | M954C1074 | M9184D1021 | N/A | 220736A | N/A | 160° | N/A | 24 | 150 | 160 | 60 | 1 | N/A | N/A | 135 ohm | M9184F1034 | N/A | FALSE
[24 empty] | 1248 | M954C1082 | M9184D1021 | N/A | 220736A | N/A | 90° | N/A | 24 | 75 | 90 | 30 | 1 | N/A | N/A | 135 ohm | M9184F1034 | Cleaver Brooks Special | FALSE
[24 empty] | 1249 | M954C4003 | M9184D1021 | N/A | 220736A | N/A | ADJ | 160° | 24 | 150 | 90/160 | 30/60 | 1 | N/A | N/A | 135 ohm | NDR | N/A | FALSE
[24 empty] | 1250 | M954D1008 | M9184D1021 | N/A | 220736B | N/A | ADJ | N/A | 24 | 150 | 90/160 | 30/60 | 2 | N/A | N/A | 135 ohm | M9184F1034 | N/A | FALSE
[24 empty] | 1251 | M954D1016 | M9184D1021 | N/A | 220736B | N/A | ADJ | N/A | 24 | 150 | 90/160 | 30/60 | 2 | N/A | N/A | 135 ohm | M9184F1034 | N/A | FALSE
[24 empty] | 1252 | M954G1052 | NDR | N/A | N/A | N/A | N/A | N/A | 220 | 50 | 160 | 60 | N/A | N/A | N/A | Series 62 | NDR | N/A | FALSE
[24 empty] | 1253 | M955A1008 | M9185D1004 | N/A | N/A | N/A | ADJ | N/A | 24 | 50 | 90/160 | 30/60 | N/A | N/A | N/A | 135 ohm | M9185D1004 | N/A | FALSE
[24 empty] | 1254 | M955A1016 | M9185D1004 | N/A | N/A | N/A | ADJ | N/A | 24 | 50 | 90/160 | 30/60 | N/A | N/A | N/A | 135 ohm | M9185D1004 | N/A | FALSE
[24 empty] | 1255 | M955A1024 | M9185D1004 | N/A | N/A | N/A | ADJ | N/A | 24 | 50 | 90/160 | 30/60 | N/A | N/A | N/A | 135 ohm | M9185D1004 | N/A | FALSE
[24 empty] | 1256 | M955A1032 | M9185D1004 | N/A | N/A | N/A | ADJ | N/A | 24 | 50 | 90/160 | 30/60 | N/A | N/A | N/A | 135 ohm | M9185D1004 | N/A | FALSE
[24 empty] | 1257 | M955B1007 | M9185D1004 | N/A | 220736B | N/A | ADJ | N/A | 24 | 50 | 90/160 | 30/60 | 2 | N/A | N/A | 135 ohm | M9185E1019 | N/A | FALSE
[24 empty] | 1258 | M955C1006 | M9185D1004 | N/A | 220736A | N/A | ADJ | N/A | 24 | 50 | 90/160 | 30/60 | 1 | N/A | N/A | 135 ohm | M9185E1019 | N/A | FALSE
[24 empty] | 1259 | M955C1014 | M9185D1004 | N/A | 220736A | N/A | ADJ | N/A | 24 | 50 | 90/160 | 30/60 | 1 | N/A | N/A | 135 ohm | M9185E1019 | N/A | FALSE
[24 empty] | 1260 | M955C4000 | M9185D1004 | N/A | 220736A | N/A | ADJ | N/A | 24 | 50 | 90/160 | 30/60 | 1 | N/A | N/A | 135 ohm | M9185E1019 | Tradeline shaft not tapped | FALSE
[24 empty] | 1261 | M955D1005 | M9185D1004 | N/A | N/A | N/A | 160° | N/A | 24 | 50 | 160 | 60 | N/A | N/A | N/A | 135 ohm | M9185A1018 | N/A | FALSE
[24 empty] | 1262 | M955D1013 | M9185D1004 | N/A | N/A | N/A | 90° | N/A | 24 | 50 | 90 | 30 | N/A | N/A | N/A | 135 ohm | M9185A1018 | N/A | FALSE
[24 empty] | 1263 | M955D1039 | M9185D1004 | 50017460-003 | N/A | N/A | 90° | N/A | 120 | 50 | 90 | 30 | N/A | N/A | N/A | 135 ohm | NDR | N/A | FALSE
[24 empty] | 1264 | M955D1047 | M9185D1004 | N/A | N/A | N/A | 90° | N/A | 24 | 50 | 90 | 30 | N/A | N/A | N/A | 135 ohm | M9185A1018 | Lennox Special | FALSE
[24 empty] | 1265 | M955D1054 | M9185D1004 | N/A | N/A | N/A | 90° | N/A | 24 | 50 | 90 | 30 | N/A | N/A | N/A | 135 ohm | M9184A1019 | York Special | FALSE
[24 empty] | 1266 | M955E1004 | M9185D1004 | 50017460-003 | 220736A | N/A | 90° | N/A | 120 | 50 | 90 | 30 | 1 | N/A | N/A | 135 ohm | NDR | N/A | FALSE
[24 empty] | 1267 | M955E1012 | M9185D1004 | 50017460-003 | 220736A | Q209E1010 | 90° | N/A | 120 | 50 | 90 | 30 | 1 | N/A | N/A | 135 ohm | NDR | Trane Special | FALSE
[24 empty] | 1268 | M965A1007 | M9185D1004 | N/A | N/A | N/A | 160° | N/A | 24 | 25 | 160 | 40 | N/A | N/A | N/A | 135 ohm | M9185D1004 | N/A | FALSE
[24 empty] | 1269 | M965A1015 | M9185D1004 | N/A | N/A | N/A | 160° | N/A | 24 | 25 | 160 | 40 | N/A | N/A | N/A | 135 ohm | M9185D1004 | N/A | FALSE
[24 empty] | 1270 | M965A1023 | M9185D1004 | 50017460-003 | N/A | N/A | 160° | N/A | 120 | 25 | 160 | 40 | N/A | N/A | N/A | 135 ohm | NDR | N/A | FALSE
[24 empty] | 1271 | M965A1031 | M9185D1004 | 50017460-003 | N/A | N/A | 90° | N/A | 120 | 25 | 90 | 23 | N/A | N/A | N/A | 135 ohm | NDR | York Special | FALSE
[24 empty] | 1272 | M965A1049 | M9185D1004 | 50017460-003 | N/A | N/A | 90° | N/A | 120 | 25 | 90 | 23 | N/A | N/A | N/A | 135 ohm | M9185D1004 | N/A | FALSE
[24 empty] | 1273 | M965A1064 | M9185D1004 | N/A | N/A | N/A | 90° | N/A | 24 | 25 | 90 | 23 | N/A | N/A | N/A | 135 ohm | M9185D1004 | N/A | FALSE
[24 empty] | 1274 | M965A1072 | M9185D1004 | N/A | N/A | N/A | 90° | N/A | 24 | 25 | 90 | 23 | N/A | N/A | N/A | 135 ohm | M9185D1004 | N/A | FALSE
[24 empty] | 1275 | M965B1006 | M9185D1004 | N/A | 220736B | N/A | 160° | N/A | 24 | 25 | 160 | 40 | 2 | N/A | N/A | 135 ohm | NDR | N/A | FALSE
[24 empty] | 1276 | M965B1014 | M9185D1004 | 50017460-001 | 220736B | N/A | 90° | N/A | 240 | 25 | 90 | 23 | 2 | N/A | N/A | 135 ohm | NDR | N/A | FALSE
[24 empty] | 1277 | M965B1022 | M9185D1004 | N/A | 220736A | N/A | 90° | N/A | 24 | 25 | 90 | 23 | 1 | N/A | N/A | 135 ohm | NDR | N/A | FALSE
[24 empty] | 1278 | M965B1030 | M9185D1004 | N/A | 220736B | N/A | 160° | N/A | 24 | 25 | 160 | 40 | 2 | N/A | N/A | 135 ohm | NDR | Reznor Special | FALSE
[24 empty] | 1279 | M975A1006 | M9185D1004 | N/A | N/A | N/A | 160° | N/A | 24 | 25 | 160 | 40 | N/A | N/A | N/A | 135 ohm | M9185D1004 | N/A | FALSE
[24 empty] | 1280 | M975A1014 | M9185D1004 | N/A | N/A | N/A | 90° | N/A | 24 | 25 | 90 | 23 | N/A | N/A | N/A | 135 ohm | M9185D1004 | N/A | FALSE
[24 empty] | 1281 | M975A1022 | M9185D1004 | 50017460-003 | N/A | N/A | 160° | N/A | 120 | 25 | 160 | 40 | N/A | N/A | N/A | 135 ohm | M9185D1004 | N/A | FALSE
[24 empty] | 1282 | M975A1030 | M9185D1004 | 50017460-003 | N/A | Q209E1010 | 90° | N/A | 120 | 25 | 90 | 23 | N/A | N/A | N/A | 135 ohm | NDR | Trane Special | FALSE
[24 empty] | 1283 | M975A1055 | M9185D1004 | 50017460-003 | N/A | Q209E1010 | 160° | N/A | 120 | 25 | 160 | 40 | N/A | N/A | N/A | 135 ohm | NDR | Carrier Special | FALSE
[24 empty] | 1284 | M975A1071 | M9185D1004 | N/A | N/A | N/A | 160° | N/A | 24 | 25 | 160 | 40 | N/A | N/A | N/A | 135 ohm | M9185D1004 | Carrier Special | FALSE
[24 empty] | 1285 | M975A1089 | M9185D1004 | N/A | N/A | N/A | 160° | N/A | 24 | 25 | 160 | 40 | N/A | N/A | N/A | 135 ohm | M9185D1004 | N/A | FALSE
[24 empty] | 1286 | M975A1097 | M9185D1004 | 50017460-003 | N/A | N/A | 160° | N/A | 120 | 25 | 160 | 40 | N/A | N/A | N/A | 135 ohm | M9185D1004 | N/A | FALSE
[24 empty] | 1287 | M975B1005 | M9185D1004 | N/A | 220736B | N/A | 160° | N/A | 24 | 25 | 160 | 40 | 2 | N/A | N/A | 135 ohm | NDR | N/A | FALSE
[24 empty] | 1288 | M975B1013 | M9185D1004 | 50017460-001 | 220736B | N/A | 160° | N/A | 240 | 25 | 160 | 40 | 2 | N/A | N/A | 135 ohm | NDR | N/A | FALSE
[24 empty] | 1289 | M975B1021 | M9185D1004 | 50017460-003 | 220736A | Q209E1010 | 90° | N/A | 120 | 25 | 90 | 23 | 1 | N/A | N/A | 135 ohm | NDR | Trane Special | FALSE
[24 empty] | 1290 | M975B1039 | M9185D1004 | 50017460-003 | 220736B | Q209E1010 | 160° | N/A | 120 | 25 | 160 | 40 | 2 | N/A | N/A | 135 ohm | NDR | Carrier Special | FALSE
[24 empty] | 1291 | M975B1047 | M9185D1004 | 50017460-003 | 220736B | N/A | 90° | 35° | 120 | 25 | 90 | 23 | 2 | N/A | N/A | 135 ohm | NDR | Trane Special | FALSE
[24 empty] | 1292 | M975B1062 | M9185D1004 | 50017460-003 | 220736B | N/A | 90° | 35° | 120 | 25 | 90 | 23 | 2 | N/A | N/A | 135 ohm | NDR | N/A | FALSE
[24 empty] | 1293 | M984B1015 | NDR | N/A | N/A | N/A | N/A | N/A | 24 | 45 | 90° | 18 | 1 | N/A | N/A | 135 ohm | NDR | N/A | FALSE
[24 empty] | 1294 | M986A1011 | NDR | N/A | N/A | N/A | N/A | N/A | 24 | 45 | 90° | 18 | N/A | N/A | N/A | 135 ohm | NDR | N/A | FALSE
[24 empty] | 1295 | M986B1002 | NDR | N/A | N/A | N/A | N/A | N/A | 24 | 45 | 90° | 18 | 1 | N/A | N/A | 135 ohm | NDR | N/A | FALSE
[24 empty] | 1296 | MA-12313 | NDR | N/A | N/A | N/A | N/A | N/A | 24 | 25 | 75 -- 180° | 28 | N/A | N/A | N/A | SPST | M8415A1004 | N/A | FALSE
[24 empty] | 1297 | MA-12323 | NDR | N/A | N/A | N/A | N/A | N/A | 24 | 25 | 75 -- 180° | 28 | 2 | N/A | N/A | SPST | M8415A1004 | N/A | FALSE
[24 empty] | 1298 | MA-305 | NDR | N/A | N/A | N/A | N/A | N/A | 24 | 16 | 180° | 20 | N/A | N/A | N/A | SPST | M836A1042 | N/A | FALSE
[24 empty] | 1299 | MA-305-500 | N/A | N/A | N/A | N/A | N/A | N/A | 24 | 16 | 180° | 20 | 1 | N/A | N/A | SPST | M836A1042 | N/A | FALSE
[24 empty] | 1300 | MA-318 | M8185D1006 | N/A | N/A | N/A | 160° | N/A | 24 | 60 | 180° | 20 | N/A | N/A | N/A | SPST | M8185D1006 | N/A | FALSE
[24 empty] | 1301 | MA-318-500 | M8185D1006 | N/A | 220736A | N/A | 160° | N/A | 24 | 60 | 180° | 20 | 1 | N/A | N/A | SPST | NDR | N/A | FALSE
[24 empty] | 1302 | MA-405 | NDR | N/A | N/A | N/A | N/A | N/A | 120 | 16 | 180° | 20 | N/A | N/A | N/A | SPST | M436A1116 | N/A | FALSE
[24 empty] | 1303 | MA-405-500 | NDR | N/A | N/A | N/A | N/A | N/A | 120 | 16 | 180° | 20 | 1 | N/A | N/A | SPST | M436A1116 | N/A | FALSE
[24 empty] | 1304 | MA-406 | NDR | N/A | N/A | N/A | N/A | N/A | 208 | 16 | 180° | 20 | N/A | N/A | N/A | SPST | M836A1042 | N/A | FALSE
[24 empty] | 1305 | MA-406-500 | NDR | N/A | N/A | N/A | N/A | N/A | 208 | 16 | 180° | 20 | 1 | N/A | N/A | SPST | M836A1042 | N/A | FALSE
[24 empty] | 1306 | MA-407 | NDR | N/A | N/A | N/A | N/A | N/A | 240 | 16 | 180° | 20 | N/A | N/A | N/A | SPST | M436A1124 | N/A | FALSE
[24 empty] | 1307 | MA-407-500 | NDR | N/A | N/A | N/A | N/A | N/A | 240 | 16 | 180° | 20 | 1 | N/A | N/A | SPST | M436A1124 | N/A | FALSE
[24 empty] | 1308 | MA-416 | M8185D1006 | 50017460-001 | N/A | N/A | 160° | N/A | 208 | 60 | 180° | 20 | N/A | N/A | N/A | SPST | M4185B1058 + 220736A | M8185D: 60 second | FALSE
[24 empty] | 1309 | MA-416-500 | M8185D1006 | 50017460-001 | 220736A | N/A | 160° | N/A | 208 | 60 | 180° | 20 | 1 | N/A | N/A | SPST | M4185B1058 + 220736A | M8185D: 60 second | FALSE
[24 empty] | 1310 | MA-418 | M8185D1006 | 50017460-003 | N/A | N/A | 160° | N/A | 120 | 60 | 180° | 20 | N/A | N/A | N/A | SPST | M4185A1001 | M8185D: 60 second | FALSE
[24 empty] | 1311 | MA-418-500 | M8185D1006 | 50017460-003 | 220736A | N/A | 160° | N/A | 120 | 60 | 180° | 20 | 1 | N/A | N/A | SPST | M4185B1009 | M8185D: 60 second | FALSE
[24 empty] | 1312 | MA-419 | M8185D1006 | 50017460-001 | N/A | N/A | 160° | N/A | 240 | 60 | 180° | 20 | N/A | N/A | N/A | SPST | M4185B1058 + 220736A | Tradeline is 60 second | FALSE
[24 empty] | 1313 | MA-419-500 | M8185D1006 | 50017460-001 | 220736A | N/A | 160° | N/A | 240 | 60 | 180° | 20 | 1 | N/A | N/A | SPST | M4185B1058 + 220736A | Tradeline is 60 second | FALSE
[24 empty] | 1314 | MA-5330 | NDR | N/A | N/A | N/A | N/A | N/A | 120 | 20 | 2" | N/A | N/A | N/A | N/A | SPST | NDR | N/A | FALSE
[24 empty] | 1315 | MA-5333 | NDR | N/A | N/A | N/A | N/A | N/A | 24 | 20 | 2" | N/A | N/A | N/A | N/A | SPST | NDR | N/A | FALSE
[24 empty] | 1316 | MA5-419 | M8185D1006 | 50017460-001 | N/A | N/A | 160° | N/A | 240 | 60 | 170° | 20 | N/A | N/A | N/A | SPST | M4185B1058 + 220736A | Tradeline is 240 second | FALSE
[24 empty] | 1317 | MA5-419-500 | M8185D1006 | 50017460-001 | 220736A | N/A | 160° | N/A | 240 | 60 | 170° | 20 | 1 | N/A | N/A | SPST | M4185B1058 + 220736A | Tradeline is 240 second | FALSE
[24 empty] | 1318 | MC-351 | M6194D1017 | N/A | 220736A | N/A | 160° | N/A | 24 | 220 | 180° | 70 | 1 | N/A | N/A | SPDT | NDR | Tradeline is 240 second | FALSE
[24 empty] | 1319 | MC-421 | M6184D1035 | 50017460-003 | 220736A | N/A | 160° | N/A | 120 | 175 | 180° | 20 | 1 | N/A | N/A | SPDT | NDR | Tradeline is 60 second | FALSE
[24 empty] | 1320 | MC-431 | M6194D1017 | 50017460-001 | 220736A | N/A | 160° | N/A | 120 | 220 | 180° | 30 | 1 | N/A | N/A | SPDT | NDR | Tradeline is 240 second | FALSE
[24 empty] | 1321 | MC-4311 | M6194D1017 | 50017460-001 | 220736A | N/A | 160° | N/A | 240 | 220 | 180° | 30 | 1 | N/A | N/A | SPDT | NDR | Tradeline is 240 second | FALSE
[24 empty] | 1322 | MC5-4311 | M6194D1017 | 50017460-001 | 220736B | 220738A | 160° | N/A | 120 | 220 | 180° | 36 | 1 | N/A | N/A | SPDT | NDR | Tradeline is 240 second | FALSE
[24 empty] | 1323 | MC-9610 | NDR | N/A | N/A | N/A | N/A | N/A | 120 | 1100 | 180° | 65 | 1 | N/A | N/A | SPDT | NDR | N/A | FALSE
[24 empty] | 1324 | MC-9810 | NDR | N/A | N/A | N/A | N/A | N/A | 120 | 1300 | 180° | 115 | 1 | N/A | N/A | SPDT | NDR | N/A | FALSE
[24 empty] | 1325 | ME-12313 | NDR | N/A | N/A | N/A | N/A | N/A | 24 | 25 | 110° | 28 | N/A | N/A | N/A | 3 position | M8405A1006 | N/A | FALSE
[24 empty] | 1326 | ME-12313-102 | NDR | N/A | N/A | N/A | N/A | N/A | 24 | 25 | 110° | 28 | 2 | N/A | N/A | 3 position | M8405A1006 | N/A | FALSE
[24 empty] | 1327 | ML984A1030 | NDR | N/A | N/A | N/A | N/A | N/A | 24 | 160 | .75" | 60 | N/A | N/A | N/A | 135 ohm | NDR | N/A | FALSE
[24 empty] | 1328 | ML984B1004 | NDR | N/A | N/A | N/A | N/A | N/A | 24 | 80 | .75" | 75 | N/A | N/A | N/A | 135 ohm | NDR | N/A | FALSE
[24 empty] | 1329 | MP-2110 | NDR | N/A | N/A | N/A | N/A | N/A | 120 | 50 | 180° | 25 | 1 | N/A | N/A | CP-8000 | NDR | N/A | FALSE
[24 empty] | 1330 | MP-2113-500 | M6184D1035 | N/A | 220736A | N/A | 160° | N/A | 24 | 50 | 180° | 25 | 1 | N/A | N/A | SPDT | M6184D1001 | Tradeline is 60 second, 150 lb-in | FALSE
[24 empty] | 1331 | MP-2130-500 | M6184D1035 | 50017460-003 | 220736A | N/A | 90° | N/A | 120 | 50 | 90° | 13 | 1 | N/A | N/A | SPDT | M6184D1001 | Tradeline is 60 second, 150 lb-in | FALSE
[24 empty] | 1332 | MP-2150-500 | M6184D1035 | 50017460-003 | 220736A | N/A | 160° | N/A | 120 | 50 | 180° | 25 | 1 | N/A | N/A | SPDT | M6184A1023 | Tradeline is 60 second, 150 lb-in | FALSE
[24 empty] | 1333 | MP-2151-500 | M6184D1035 | 50017460-001 | 220736A | N/A | 160° | N/A | 240 | 50 | 180° | 30 | 1 | N/A | N/A | SPDT | NDR | Tradeline is 60 second, 150 lb-in | FALSE
[24 empty] | 1334 | MP-371 | M6294D1008 | N/A | 220736A | N/A | 160° | N/A | 24 | 50 | 180° | 90 | 1 | N/A | N/A | SPDT | NDR | Tradeline is 160°, 240 second | FALSE
[24 empty] | 1335 | MP-381 | M6194D1017 | N/A | 220736A | N/A | 160° | N/A | 24 | 220 | 180° | 130 | 1 | N/A | N/A | SPDT | NDR | Tradeline is 160°, 240 second | FALSE
[24 empty] | 1336 | MP-481 | M9194D1003 | 50017460-003 | 220736A | Q7230A1005 | 160° | N/A | 120 | 220 | 180° | 130 | 1 | N/A | N/A | 2-15 Vdc | NDR | Set signal range | FALSE
[24 empty] | 1337 | MP-483-600 | M6294D1008 | 50017460-003 | 220736A | N/A | 90° | N/A | 120 | 220 | 90° | 65 | 1 | N/A | N/A | SPDT | M6294D1008 | Check timing and stroke | FALSE
[24 empty] | 1338 | MP-485 | M6194D1017 | 50017460-003 | 220736A | N/A | 160° | N/A | 120 | 220 | 180° | 130 | 1 | N/A | N/A | SPDT | NDR | Check timing and stroke | FALSE
[24 empty] | 1339 | MP-4851 | M6294D1008 | 50017460-001 | 220736A | N/A | 160° | N/A | 240 | 220 | 180° | 130 | 1 | N/A | N/A | CP-8000 | NDR | Check timing and stroke | FALSE
[24 empty] | 1340 | MP-486 | M6294D1008 | 50017460-003 | 220736A | N/A | 160° | N/A | 120 | 220 | 180° | 130-1300 | 1 | N/A | N/A | SPDT | NDR | Check timing and stroke | FALSE
[24 empty] | 1341 | MP-9710 | NDR | N/A | N/A | N/A | N/A | N/A | 120 | 800 | 180° | 135 | 1 | N/A | N/A | Proportional | NDR | N/A | FALSE
[24 empty] | 1342 | MU-12313 | NDR | N/A | N/A | N/A | N/A | N/A | 24 | 25 | 90° | 28 | N/A | N/A | N/A | Economizer | M7415A1006 | N/A | FALSE
[24 empty] | 1343 |  |  | FALSE FALSE: FALSE
1344
1345
1346
1347
1348
1349
1350
1351
1352
1353
1354
1355
1356
1357
1358
1359
1360
1361
1362
1363

## FINDINV1
Modutrol IV Motor Cross Reference
REPLACE THIS MOTOR (scroll below to find)
Select model
(scroll below to find)
Original Motor Specifications
| AUX SWITCH SETTINGS | VOLT (vac) | TORQUE (lb-in, lb-ft) | STROKE MAX (DEGREES) | TIMING MAX (SEC) | AUX SWITCHES | MOTOR SHAFTS | ADAPTOR BRACKET | CONTROL SIGNAL
Select model | - | - | - | - | - | - | - | - | -
Configure TRADELINE Replacement as described below
| MOD IV TRADELINE REPLACEMENT | REQ. TRANS-FORMER | REQUIRED AUX SWITCH | REQUIRED ACCESSORIES | SET STROKE SETTING *
How to use this Cross Reference | - | - | - | - | -
* ADJ indicates original motor has adjustable stroke
Cross Reference Format | FUNCTIONAL REPLACEMENT
-
Application Notes
COMMENTS
-
Printed version Modutrol IV Motor Cross Reference available at
http://hbctechlit.honeywell.com